## Slide 1: OpenDSS Example Scripts Version 1
Speaker’s Name Robert Arritt
Event 6/5/2013

## Slide 2: Open-Phase Analysis
Example of a delta-wye (3-legged core design)

## Slide 3: Master File
Be sure to add no-load losses.
Clear
New Circuit.OpenPhaseTest
~ Bus1=MainBus BasekV=230 pu=1.0 Isc3=15000 Isc1=17000 X1R1=30 X0R0=30
// ---------------------- 3-Legged Core Delta-Y ----------------------
New Reactor.DY3LegLink Phases=3 Bus1=mainBus.1.2.3 Bus2=DY3legPri.1.2.3 R=0 X=0.001
New Transformer.DY3Leg Windings=3 XHL=10 XHT=100 XLT=80 %imag=0.5 %noloadloss=0.5
~ Buses=[DY3legPri.1.2.3 DY3legBus.1.2.3.4 DY3legPhantom]
~ kVs=[230 4.16 4.16]
~ conns=[Delta Wye Delta]
~ kvas=[25000 25000 25000] %LoadLoss=0.2
// Neutral Resistor
New Reactor.Rneut3DY Phases=1 bus1=DY3legBus.4 Bus2=DY3legBus.0 R=20 X=0
Set voltagebases=[345, 230 13.2 4.16]
Calcvoltagebases
Solve

## Slide 4: Run File
Run file to edit reactor to place open phase with no load
/ Open Phase Case no load
Compile Master.DSS
Set Case=open_NOload
// Open Phase A
Reactor.DY3LegLink.Bus1=MainBus.31.2.3 Bus2=DY3legPri.1.2.3
New Monitor.DY3LegLink Element=Reactor.DY3LegLink Terminal=2 mode=16
New Monitor.Secondary_DY3LEG Element=TRANSFORMER.DY3LEG Terminal=2 mode=16
solve
Show Voltage LN Nodes
Edit Reactor to place line on Open Node
31 1

## Slide 5: Results
NODE-GROUND VOLTAGES BY BUS & NODE
Bus Node V (kV) Angle p.u. Base kV
MAINBUS ..... 1 132.79 /_ 0.0 1 230.000
- 2 132.79 /_ -120.0 0.99999 230.000
- 3 132.79 /_ 120.0 0.99998 230.000
- 31 66.392 /_ -180.0 0.49997 230.000
DY3LEGPRI ... 1 66.392 /_ -180.0 0.49997 230.000
- 2 132.79 /_ -120.0 0.99999 230.000
- 3 132.79 /_ 120.0 0.99998 230.000
DY3LEGBUS ... 1 1.2003 /_ -90.0 0.49975 4.160
- 2 1.2002 /_ -90.0 0.49972 4.160
- 3 2.4005 /_ 90.0 0.99947 4.160
- 4 1.0354E-013 /_ -1.4 4.31E-014 4.160
DY3LEGPHANTOM 1 5.6543E-005 /_ -45.0 2.35E-005 4.160
- 2 2.0784 /_ -90.0 0.86534 4.160
- 3 2.0784 /_ 90.0 0.86536 4.160

## Slide 6: Add Load to Open Phase Case
Sequence Load
Add command to Run file
New REACTOR.DY3Leg Phases=3 Bus1= DY3legBus.1.2.3 Bus2=DY3legBus.6.6.6 kV=4.16
~ conn=wye Z1=[5.94 4.04] Z2=[0.36 1.09] Z0=[1000000 10000000]
Redirect load.dss
R1 X1
R2 X2
R0 X0

## Slide 7: Results
NODE-GROUND VOLTAGES BY BUS & NODE
Bus Node V (kV) Angle p.u. Base kV
MAINBUS ..... 1 132.79 /_ 0.0 1 230.000
- 2 132.77 /_ -120.0 0.99986 230.000
- 3 132.71 /_ 120.0 0.99938 230.000
- 31 86.333 /_ -22.1 0.65015 230.000
DY3LEGPRI ... 1 86.333 /_ -22.1 0.65015 230.000
- 2 132.77 /_ -120.0 0.99986 230.000
- 3 132.71 /_ 120.0 0.99938 230.000
DY3LEGBUS ... 1 2.1477 /_ -45.3 0.89423 4.160
- 2 1.7617 /_ -151.3 0.73349 4.160
- 3 2.3721 /_ 89.2 0.98762 4.160
- 4 1.144E-013 /_ -47.9 4.76E-014 4.160
- 6 5.8046E-010 /_ -101.4 2.41E-010 4.160
DY3LEGPHANTOM 1 1.808 /_ -12.5 0.75276 4.160
- 2 2.0651 /_ -116.6 0.85984 4.160
- 3 2.3904 /_ 110.6 0.99528 4.160

## Slide 8: Add Daily Load Shape to 13-Bus Test Feeder
Set Up Edit File
  Could Change Every Load Definition (Not Recommended)
  Select Loads and Go to Show>Elements in Class
Edit Load.671 Bus1=671.1.2.3 Phases=3 Conn=Delta Model=1 kV=4.16 kW=1155 kvar=660 Daily=Default
…
671
634A
634B
634C
645
646
692
675A
675B
675C
611
652
670A
670B
670C
Use Text Editor
Load.671.Daily=Default
Load.634A.Daily=Default
Load.634B.Daily=Default
Load.634C.Daily=Default
Load.645.Daily=Default
Load.646.Daily=Default
Load.692.Daily=Default
Load.675A.Daily=Default
Load.675B.Daily=Default
Load.675C.Daily=Default
Load.611.Daily=Default
Load.652.Daily=Default
Load.670A.Daily=Default
Load.670B.Daily=Default
Load.670C.Daily=Default

## Slide 9: Or Use Batch Command
Add Monitor
Redirect IEEE13Nodeckt.dss
BatchEdit Load..* daily=default
New Monitor.Sub element=Transformer.Sub terminal=2 mode=0
Solve
BusCoords IEEE13Node_BusXY.csv
set mode=daily number=24
Solve
New monitor
BatchEdit
PERL regular expression. .* matches all names
Loadshape

## Slide 10: Plot Results
Current
Chart: Time (Hour)
I1 | 381.857 | 348.593 | 338.013 | 322.353 | 320.486 | 334.346 | 368.681 | 426.755 | 482.531 | 513.413 | 553.87 | 586.806 | 584.163 | 580.748 | 587.34 | 593.561 | 594.24 | 565.939 | 551.212 | 535.852 | 511.251 | 511.248 | 479.611 | 432.24
I2 | 283.596 | 260.435 | 252.793 | 240.835 | 239.494 | 249.449 | 274.12 | 315.84 | 354.901 | 378.1 | 406.043 | 429.47 | 427.56 | 425.157 | 429.852 | 434.267 | 434.746 | 414.632 | 404.14 | 393.2 | 375.672 | 375.672 | 353.07 | 319.912
I3 | 396.221 | 362.136 | 350.979 | 334.487 | 332.534 | 347.058 | 383.244 | 444.94 | 503.282 | 537.921 | 581.502 | 616.994 | 614.168 | 610.474 | 617.572 | 624.288 | 625.027 | 594.507 | 578.649 | 562.113 | 535.647 | 535.636 | 501.7 | 450.959

## Slide 11: Circuit Description Text
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
One-Line of Example
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG

## Slide 12: Source
The default source is edited.
Edit vsource.Source bus1=Sourcebus basekv=115 pu=1.025782 angle=0.0 freq=60.0 ~ phases=3 MVAsc3=20000000 MVAsc1=2100000000
Black Bold Text Typed in Script Window
Object Class
Parameters
Edit Command
Object Name
Bus object is connected
Bus Name
Allows continuation onto next line

## Slide 13: Line
Add script connecting the first line. Define line impedance by using sequence impedance.
New line.TRAP_FALLS_Feed bus1=Sourcebus bus2=TRAP_FALLS_HSB r1=1.3965 ~ x1=3.290 r0=1.730556 x0=0.062
Black Bold Text Typed in Script Window
Object Class
Impedance defined by sequence Impedance
New Command
Object Name
Buses object is connected to
Bus Name
Allows continuation onto next line (“More”)
Continuation of Parameters
Bus Name
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG

## Slide 14: Transformer
Add script adding a transformer to the circuit. Note: Tranformer’s wye connection.
New Transformer.TRAP_FALLS_XFR phases=3 windings=2 buses=(TRAP_FALLS_HSB, TRAP_FALLS_LSB.1.2.3.4) ~ conns=(Delta wye) kvs=(115, 13.8) kvas=(60000, 60000) xhl=11.7
Object Class
New Command
Object Name
Secondary Bus Name Note: Bus Connections Specified so wye connection is not defaulted to a grounded wye.
Primary Voltage
% Reactance
Primary Bus Name
Secondary Voltage
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG

## Slide 15: Neutral to Ground Reactor for Transformer
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG
New Reactor.TRAP_FALLS_X phases=1 bus1=TRAP_FALLS_LSB.4 ~ bus2=TRAP_FALLS_LSB.0 R=0 X=0.313
Connection to Transformer Secondary Bus Neutral (4)
Reactive Connection Only
Connection to Transformer Secondary Bus Ground (0)

## Slide 16: Linecode
New Linecode.UD_750EPR_3_N nphases=3 0.101 0.192 0.327 0.106 682.652 682.652 ~ Normamps=350.4 438 units=mi
New Line.Feeder1 bus1=TRAP_FALLS_LSB bus2=Bluestone length=3.78 linecode=UD_750EPR_3_N
r1
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG
x1
r0
x0
c1
c2
Linecode
Emergency Amps
Normal Amp Limit
Length in miles
Line Definition

## Slide 17: Load
New Load.Load_1 phases=3 bus1=Bluestone kv=13.8 kw=500 pf=1 conn=delta
Object Class
Load Parameters
New Command
Object Name
Bus Name
Delta Connected Load
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG

## Slide 18: Transformer and Neutral Resistance
New Transformer.Bluestone_XFR buses=(Bluestone.1.2.3.4 Bluestone_Gen) Conns=(Wye Delta) ~ kVS=(13.8 13.8) kVAs=(35000 35000) XHL=2.2
New Reactor.Bluestone_R phases=1 Bus1=Bluestone.4 Bus2=Bluestone.0 R=5.714286 X=0
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG
Resistive Component

## Slide 19: Synchronous Generator
New Generator.Bluestone_DG bus1=Bluestone_Gen kVA=35000 kV=13.8 pf=1 Xdp=0.163 Xdpp=0.163 ~ xd =0.4 model=1 conn=delta
TRAP_FALLS_FEED
Sourcebus
TRAP_FALLS_XFR
Source
TRAP_FALLS_HSB
Bluestone
Feeder1
TRAP_FALLS_X
TRAP_FALLS_LSB
Bluestone_R
Bluestone_XFR
Load_1
Bluestone_Gen
Bluestone_DG
Transient Reactance (pu)
Subtransient Reactance (pu)
Synchronous Reactance (pu)
Model 1 - Generator injects a constant kW at specified power factor

## Slide 20: Example – Master File
Save Script as ExampleDG_Master.dss
Clear
New Circuit.Example_DG
Edit vsource.source bus1=Sourcebus basekV=115 pu=1.025782 angle=0.0 freq=60 phases=3 MVAsc3=20000000 MVAsc1=21000000
New line.TRAP_FALLS_Feed bus1=Sourcebus bus2=TRAP_FALLS_HSB r1=1.3965 x1=3.290 r0=1.730556 x0=0.062
New Transformer.TRAP_FALLS_XFR phases=3 windings=2 buses=(TRAP_FALLS_HSB, TRAP_FALLS_LSB.1.2.3.4) conns=(Delta wye) kvs=(115, 13.8)
~kvas=(60000, 60000) xhl=11.7
New Reactor.TRAP_FALLS_X phases=1 bus1=TRAP_FALLS_LSB.4 bus2=TRAP_FALLS_LSB.0 R=0 X=0.313
New Linecode.UD_750EPR_3_N nphases=3 0.101 0.192 0.327 0.106 682.6525199 682.6525199 Normamps=350.4 438 units=mi
New Line.Feeder1 bus1=TRAP_FALLS_LSB bus2=Bluestone length=3.78 linecode=UD_750EPR_3_N
New Reactor.Bluestone_R phases=1 Bus1=Bluestone.4 Bus2=Bluestone.0 R=5.714286 X=0
New Transformer.Bluestone_XFR buses=(Bluestone.1.2.3.4 Bluestone_Gen) Conns=(Wye Delta) kVS=(13.8 13.8) kVAs=(35000 35000) XHL=2.2
New Generator.Bluestone_DG bus1=Bluestone_Gen kVA=35000 kV=13.8 pf=1 Xd=1 Xdp=0.163 Xdpp=0.163 model=1 conn=wye
New Load.Load_1 phases=3 bus1=Bluestone kv=13.8 kw=500 pf=1 conn=delta
Set voltagebases=(115, 13.8)

## Slide 21: Example – Script File
Open new file in the same folder to run different scripts
Now select all and select Control+D
Compile ExampleDG_Master.dss
Calcv
Solve
Show Voltage LN Nodes
summary
Example File

## Slide 22: Example – Script File, cont.
In same file run a fault mode solution
Now select fault script and select Control+D
Compile ExampleDG_Master.dss
Calcv
Solve
Set mode=fault
Calcv
Solve
show faults
Example File

## Slide 23: Example – Script File
In same file run a fault mode solution
Now select fault script and select Control+D
Compile ExampleDG_Master.dss
New fault.fbluestone bus1=Bluestone.1 bus2=Bluestone.0 phases=1
Calcv
Solve
Set Mode=Dynamics
Show Voltage LN Nodes
summary
Insert Fault Between Phase 1 and Ground

## Slide 24: Example – Script File
In same file run a fault mode solution
Now select fault script and select Control+D
Compile ExampleDG_Master.dss
Set Loadmult=1
Set Genmult=1
Edit Line.Feeder1 length=23.78
Calcv
Solve
save voltages
Disable "Generator.Bluestone_DG"
Set Controlmode=OFF
solve
Vdiff

## Slide 25: Together…Shaping the Future of Electricity