## Slide 1: OpenDSS Training Workshop
Roger C. Dugan Sr. Technical Executive
SRP/ASU Workshop, Tempe AZ 16-17 Dec 2014

## Slide 2: Agenda
Day 1
  OpenDSS Concepts
  Installation
  Basic scripting
  The COM interface
Day 2
  Loadshapes and Smart Grid Simulation
  Detailed Modeling
  COM interface example(s)
  Misc hints and tips
  DA Class Exercise

## Slide 3: Objectives of this Workshop
Provide basic training in OpenDSS usage
Provide distribution engineers with a powerful tool for dynamic distribution modeling to supplement their existing tools
Provide students:
  With a tool to complete their research
  With an understanding of power distribution systems
  With skills for the next generation power industry
    The “Integrated Grid”
Encourage students to explore and develop new concepts useful to the industry

## Slide 4: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool for dynamic distribution system modeling
Specific models for:
  Supporting utility distribution system analysis
  Initially designed for the unbalanced, multi-phase North American power distribution systems
  Can also model European-style systems
      These typically have a simpler structure

## Slide 5: What is the OpenDSS? (cont’d)
Heritage of OpenDSS
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve the power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose in 1997: DG interconnection analysis

## Slide 6: What is the OpenDSS? (cont’d)
What it is NOT
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics” mode
      All solutions are in phasors (complex math)
  Not a “Power Flow” program
  Not a radial circuit solver
    Does meshed networks with equal ease
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 7: What is the OpenDSS? (cont’d)
EPRI acquired the DSS software from Electrotek Concepts in 2004
It is EPRI’s primary tool for researching new methods in distribution system analysis
EPRI made the program open source in 2008 to collaborate with the industry to advance grid modernization efforts
User have access to the latest versions that EPRI is using
  Sourceforge.net is our source code repository

## Slide 8: Why Dynamic Distribution Modeling?
You don’t get the right answer for many issues unless you simulate over a significant period of time
  Disruptive technologies in distribution systems:
  Integration of distributed generation and storage
  Microgrids
  Electric vehicles and other load changes
Evaluation of power delivery losses

## Slide 9: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak demand capacity
  Capture mostly location-specific benefits
  Ignores time; assumes the resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do sequential-time analysis to get the right answer
  Over a distribution planning area
  Over a significant time period
    Year, Month, or Week

## Slide 10: What can OpenDSS be used for?
DG
  Interconnection studies/screening
  Value of service studies (risk based)
  Solar PV voltage rise/fluctuation
  Wind power variations impact
  Hi-penetration solar PV impacts
  Harmonic distortion
  Dynamics/islanding

## Slide 11: Program Files
For each of X86 and X64 versions:
  OpenDSS.EXE Standalone EXE
  OpenDSSEngine.DLL In-process COM server
  KLUSolve.DLL Sparse matrix solver
  DSSView.EXE is a separate program for processing graphics output

## Slide 12: User Interfaces Currently Implemented
A stand-alone executable program that provides a text-based scripting interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  32-bit and 64-bit (New in 2012)
EPRI Program 174 funders have access to DGScreener, an interface to OpenDSS

## Slide 13: Why Scripting and COM?
More flexible than static forms
No two Smart Grid simulations alike
Not possible to predict what users will want to do
  COM = Component Object Model
  Supported by nearly all programming languages, Microsoft Office, MATLAB, Python, etc
  Allows user to write their own algorithms
    For things like DA controllers and DMS simulators
    Co-simulation of power and communications
  COM is not familiar to most power engineers but is powerful means of scripting

## Slide 14: What is COM?
COM = Component Object Model
A binary-interface standard for software components introduced by Microsoft in 1993
Related technologies
  OLE, OLE Automation, ActiveX, COM+, DCOM
A language-neutral way of implementing objects that can be used in environments different from the one in which they were created
Microsoft Office tools like Excel and Work can be Automated via COM
  And VBA supports automating other apps via COM

## Slide 15: SourceForge.Net Links for OpenDSS
EPRI Links Page
  http://smartgrid.epri.com/SimulationTool.aspx
OpenDSS Download Files:
  http://sourceforge.net/projects/electricdss/files/
Top level of Main Repository

## Slide 16: Discussion Forum & News for OpenDSS

## Slide 17: Installing
EPRI Link Page
    http://smartgrid.epri.com/SimulationTool.aspx

## Slide 18: Installing
Download the Installer
  http://sourceforge.net/projects/electricdss/files/
Get pdf Files, too (Also can be found in distrib/doc folder)

## Slide 19: Registering the COM Server Manually
Registering occurs automatically when using the Installer
If you intend to drive OpenDSS from another program, you will need to register the COM server
    Some programs require this !!
    If you are sure you will only use OpenDSS.EXE, you can skip this step
      You can come back and do it at any time
In the command (cmd) window, change to the folder where you installed it and type:
  Regsvr32 OpenDSSEngine.DLL

## Slide 20: Manually Registering the COM Server – Windows 7 (Method 1)
Special instructions for Windows 7
  (and probably Windows Vista, too)
  See Q&A on the Wiki site
  http://sourceforge.net/apps/mediawiki/electricdss/index.php?title=How_Do_I_Register_the_COM_Server_DLL_on_Windows_7%3F
All Programs > Accessories
right-click on the Command Prompt and select Run as Administrator.
Then change to your OpenDSS folder and type in
  "regsvr32 OpenDSSEngine.DLL”

## Slide 21: Registering the COM Server – Windows 7, Method 2
Another Process for Windows 7
  per Andy Keane- UC Dublin
  1. Right click on the desktop and select new -> shortcut
  2. For location of item just type ‘cmd’
  3. This will create a new shortcut to a command prompt on your desktop
  4. Right click on the new shortcut and select ‘Properties’
  5. On the shortcut tab select ‘Advanced’
  6. Tick the ‘Run as Administrator’ box
  7. Press Apply/OK and that command prompt will always be run as administrator allowing the user to use regsvr32

## Slide 22: So What Did this Do?
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer
On Windows 7: 32-bit server is registered in WOW6432Node

## Slide 23: The GUID References the DLL File ….
If you look up the GUID in RegEdit
Points to OpenDSSEngine.DLL (In-process server, Apartment Threading model)

## Slide 24: 32-bit Vs 64-bit
On Windows 7 & 8 you can register both versions
  They are in separate places in the registry
  You will probably need to register both
    MATLAB is often installed as 64-bit (x64)
    MS Office is most often installed as 32-bit (x86)
Windows 7 will run the proper version depending on the type of program invoking the DSSEngine.
  Magic!!

## Slide 25: 32-bit Vs 64-bit
On Windows 7 you can register both versions
  They are in separate places in the registry
  You will probably need to register both
    MATLAB is often installed as 64-bit (x64)
    MS Office is most often installed as 32-bit (x86)
Windows 7 will run the proper version depending on the type of program invoking the DSSEngine.
  Magic!!

## Slide 26: Questions So Far?

## Slide 27: How OpenDSS Works

## Slide 28: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 29: Primitive Y Matrix
Simple Resistor

## Slide 30: Primitive Y Matrix, cont’d
LINE model

## Slide 31: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 32: The Network Model

## Slide 33: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 34: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 35: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 36: Load - 3-phase Y connected
Phase 1
Phase 2
Phase 3
3
2
1
4
4 Conductors/Terminal

## Slide 37: Load - 3-phase Delta connected
Phase 1
Phase 2
Phase 3
3
2
1
3 Conductors/Terminal

## Slide 38: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 39: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 40: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 41: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 42: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 43: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 44: Solving the Power Flow …
This solution method requires that the first guess at the voltages be close to the final solution
  Not a problem for daily or yearly simulations
    Present solution is a good guess for next time step
  First solution is often most difficult
  The solution initialization routine in OpenDSS accomplishes this with ease in most cases
Method works well for arbitrary unbalances
  For conditions that are sensitive, a Newton method is provided that is more robust, but slower.
  Not to be confused with “Newton-Raphson Power Flow”

## Slide 45: Solution Speed
Distribution systems generally converge very well
  Many transmission systems, also
The OpenDSS on par with faster commercial programs
Solution method is designed to run annual simulations
Our philosophy:
    Err on the side of running more power flow simulations
      Don’t worry about the solution time until it proves to be a problem
      This reveals more information about the problem

## Slide 46: OpenDSS Solution Loop with Controls

## Slide 47: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, SYNERGEE, WindMil, and other programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Being used to develop the DG Protection test feeder
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data.

## Slide 48: Circuit Modeling Basics
Some things that might be a bit different than other power system analysis tools you may have used.

## Slide 49: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 50: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 51: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 52: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 53: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
LOAD

## Slide 54: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load to Node 2 and ground
1-Phase Load Example

## Slide 55: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 56: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node is explicitly computed (just like any other Node)

## Slide 57: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 58: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 59: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use XfmrCode to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 60: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 61: Scripting Basics
Syntax and how to build circuit models.
Simple Model

## Slide 62: Scripting Recommendation
A good text editor is recommended
  Notepad is OK but others may be better for you:
  EditPlus
  TextPad
  Notepad++
Must be capable of saving a file in plain ANSI text
  Not Unicode
  Not RTF (Write)
  Not Doc (Word)

## Slide 63: Scripting
OpenDSS is a scriptable solution engine
Scripts
  Series of commands
  From text files
  From edit forms in OpenDSS.EXE
  From another program through COM interface
    e. g., This is how you would do looping
Scripts define circuits
Scripts control solution of circuits
Scripts specify output, etc.

## Slide 64: Command Syntax
Command parm1, parm2 parm3 parm 4 ….
Parameters may be positional or named (tagged).
If named, an "=" sign is expected.
  Name=value (this is the named form)
  Value (value alone in positional form)
For example, the following two commands are equivalent:
  New Object="Line.First Line" Bus1=b1240 Bus2=32 LineCode=336ACSR, …
  New “Line.First Line”, b1240 32 336ACSR, …
Comma or white space

## Slide 65: Delimiters
Array or string delimiter pairs: [ ] , { },( ),“ “,‘ ‘
Matrix row delimiter: |
Value delimiters: , (comma) any white space (tab or space)
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?

## Slide 66: Array and Matrix Parameters
Array
  kvs = [115, 6.6, 22]
  kvas=[20000 16000 16000]
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 67: An Example

## Slide 68: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
~ bus1=sourcebus.1.2.3 bus2=Sourcebus.10.10.10
New Reactor.Rneutral phases=1 bus1=Sourcebus.10 Bus2=Sourcebus.0 R=.01 X=0
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages
Show Currents
Show Powers kVA elements

## Slide 69: Circuit
New Circuit.Simple ! (Vsource.Source is active circuit element)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500
Source
115
kV
SourceBus
Vsource.Source
115 kV, 1.05 pu
Short Circuit Impedance (a matrix) that yields 3000A 3-ph fault current and 2500A 1-ph fault current.
One-Line Diagram (default is 3-phase wye-grd source)

## Slide 70: Vsource Element Note
Vsource is actually a Two-terminal Device
  2nd terminal defaults to connected to ground (0V)
  But you can connect it between any two buses
    Comes in handy sometimes
Conceptually a Thevinen equivalent
  Short circuit equivalent
  Actually converted to a Norton equivalent internally

## Slide 71: 20 MVA Substation Transformer
TR
1
New Transformer.TR1 Phases=3 Windings=2
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[20000 20000]
~ XHL=10
New Transformer.TR1 Phases=3 Windings=2 XHL=10
~ wdg=1 bus=SourceBus Conn=Delta kV=115 kVA=20000
~ wdg=2 bus= Sub_Bus Conn=wye kV=12.47 kVA=20000
Defining Using Arrays
Defining Winding by Winding
Sub_Bus
SourceBus

## Slide 72: The Line
LINE
1
1
Mile
,
336
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
Sub_Bus
LoadBus
Line objects may also be defined by Geometry or matrix properties.
(Rmatrix=… Xmatrix=… Cmatrix=…)

## Slide 73: The Load
Loadbus
LOAD
1
1000
kW
0
.
95
PF
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
For 3-phase loads, use L-L kV and total kW
For 1-phase loads, typically use L-N kV and total kW unless L-L-connected; Then use L-L kV.

## Slide 74: Solving and Showing Results Reports
  Solve
    Show summary (power flow summary)
  Show Voltages
  Show Currents
  Show Powers kVA elements
Also
  Export … (creates CSV files)
  Plot …

## Slide 75: Detailed Distribution Circuit Modeling
How to organize scripts for larger problems
Examination of how the IEEE 8500-Node Test Feeder model is organized

## Slide 76: Scripting Large Circuits
For small circuits, often put all the scripts in one file
  Some IEEE test feeder examples are mostly in one file
When you have large amounts of data, a more disciplined approach is recommended using multiple files:
Redirect Command
  Redirects the input to another file
  Returns to home directory
Compile Command
  Same as Redirect except repositions home directory

## Slide 77: Organizing Your Main Screen
OpenDSS.exe saves all windows on the main screen
  They appear where you left them when you shut down
  The next time you start up, you can resume your work
Values are saved in the Windows Registry
Come up with a way you are comfortable with

## Slide 78: OpenDSS Registry Entries
Certain persistent values are saved to the Windows Registry upon exiting the program
Default Editor Setting

## Slide 79: Organizing Your Main Screen
Project Run window
Main Script Window never goes away. Put some frequently-used commands here.
Plotting Scripts
Annual Simulation Script
Misc. Scripts

## Slide 80: A Common Sense Structuring of Script Files
Run_The_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Put a “Clear” in here
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Circuit Definition
“Compile” the Master file from here
Make a separate folder for each circuit

## Slide 81: Organizing Run Scripts
Compiles the Circuit Description
Override Some Property Settings and/or Define Some Additional Circuit Element
Change an option
Solve Snapshot Power Flow
Selected Results Display
Based on 123-bus Test Feeder

## Slide 82: Organizing Your Master File
So Compile Doesn’t Fail
General Library Data
Circuit Elements for this Model
Let OpenDSS Define the Voltage Bases
(You can do this explicitly with SetkVBase command)

## Slide 83: Example: IEEE 8500-Node Test Feeder

## Slide 84: Main Part of “Run” File
Compile (C:\DSSdata\IEEETest\8500Node\Master-unbal.dss)
! Put an Energymeter at the head of the feeder New Energymeter.m1 Line.ln5815900-1 1
! Sometimes the solution takes more than the default 15 iterations Set Maxiterations=20
Solve
Compile base circuit description
Add an energymeter not in base description
Change an option
Solve

## Slide 85: The Master File
Clear
New Circuit.IEEE8500u
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.dss
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
Redirect LoadXfmrs.dss ! Load Transformers
Redirect Triplex_Lines.dss
Redirect UnbalancedLoads.dss
Redirect Capacitors.dss
Redirect CapControls.dss
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordintes now that bus list is established
Buscoords Buscoords.dss

## Slide 86: Loadshapes and Smart Grid Simulation
How to use the OpenDSS Loadshape capability and simulate various time-series phenomena related to Smart Grid simulations.

## Slide 87: Loadshapes
Key feature of OpenDSS
  Efficient execution of time-varying loads, generation is accomplished through Loadshape objects
Sequential time simulation is required for many Smart Grid analyses
Basic time-varying modes that use Loadshape objects
  Daily (nominally 24 h, 1 h steps)
  Yearly (nominally 8760 h, 1 h steps)
  Dutycycle (nominal step size 1 s .. 5 m)
    (used for wind and solar)
Learning to work with Loadshapes is an essential skill for OpenDSS users

## Slide 88: Example Loadshape for Wind Turbine Output
Watts
Vars

## Slide 89: Example Loadshapes Provided in Examples Folder

## Slide 90: How to Define
Clear
! Example scripts for loading and plotting loadshapes out of the loadshape library
! You have to have a circuit defined to load in loadshapes.
New Circuit.LoadshapeExamples
! directly ...
New "LoadShape.LoadShape1a" npts=8760 interval=1.0 mult=(File=LoadShape1.csv)
Plot Loadshape Object=Loadshape1a ! execute this to prove you got it
! or using Redirect
Redirect Loadshape1.DSS ! Load in Loadshape 1
Plot Loadshape Object=Loadshape1

## Slide 91: Example Yearly LoadShape

## Slide 92: Loadshape Interpolation
The OpenDSS LOADSHAPE class uses two different types of interpolation depending on it is defined
Fixed interval data.
  Default: INTERVAL property defaults to 1 hour.
  You can set it to another value or to 0.
    The SINTERVAL and MINTERVAL properties facilitate defining intervals in Seconds or Minutes.
  INTERVAL > 0 means fixed interval data
    CSV files --one numeric value per line.
    Value REMAINS CONSTANT over the entire interval
    The HOUR array property is ignored

## Slide 93: Loadshape Interpolation, Cont’d
For LINEAR INTERPOLATION between the points, define INTERVAL=0.
  Then both the time and multiplier values for the loadshape using the HOUR, MULT, and QMULT array properties.
Alternatively, you may use the CSVFILE, DBLFILE, or SNGFILE properties.
  Enter both the time in hours and the multiplier values.
    A CSV file would have two values per line separated by a comma or whitespace.
The variable interval interpolation could be a little bit slower than the fixed interval data because there is more work to do to compute the factor.

## Slide 94: Importing Packed Binary Files
For simulations, such as AMI, required large volumes of Loadshapes to be imported, using packed binary files can save time
Standard CSV or TXT file
  Mult=[file=myfile.txt]
File of doubles
  Mult=[dblfile=myfile.dbl]
File of singles
  Mult=[sngfile=myfile.sng]

## Slide 95: Recent (2011) Enhancements to Defining Array Properties Using CSV files
Syntax:
  mult=[File=myMultiColumnFile.CSV, Column=n, Header=Yes/No]
Allows use of multicolumn CSV files
  with a single header row.
Example:
New Loadshape.Ramp2 npts=4000 sInterval=1 mult=(file=MultiChannelTest.csv, column=3, header=yes)
  Imports the 3rd column from the file, skipping the header row

## Slide 96: OpenDSS COM Interface
Programming via the COM interface

## Slide 97: Review: Two Implementations of OpenDSS
Stand-alone EXE
  32-bit
  64-bit
  Use this to develop text scripts to study problems
In-Process COM Server
  32-bit
  64-bit
  Use this to link OpenDSS to other programs
    Automate the program
    Execute complex algorithms

## Slide 98: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs
Text

## Slide 99: OpenDSSEngine.DSS is Registered
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 100: Linking Your Program to the COM Server
Examples of accessing the COM server in various languages
In MATLAB:
  DSSobj = actxserver(‘OpenDSSEngine.DSS’);
In VBA:
  Public DSSobj As OpenDSSEngine.DSS Set DSSobj = New OpenDSSEngine.DSS
In Dephi
  {Import Type Library}
  Type DSSObj : IDSS;
  …
  DSSObj := coDSS.Create;

## Slide 101: Linking Your Program to the COM Server, 2
In PYTHON:
  Import win32com.client
  Class DSS:
  self.engine = win32com.client.Dispatch("OpenDSSEngine.DSS")
In C#:
  (Project >Add Reference … select OpenDSSEngine)
  Using OpenDSSEngine;
  Public DSS DSSObj;
  DSSObj = new DSS();

## Slide 102: OpenDSS COM Interfaces
There are many interfaces supplied by the COM server
There is one registered In-Process COM interface:
  OpenDSSEngine.DSS
    The DSS interface is the one your program instantiates
    The DSS interface then creates all the others.
    This is for simplicity for users who are not necessarily familiar with COM programming

## Slide 103: “Active objects” concept
.The interfaces generally act on the ACTIVE object
  Active circuit,
  Active circuit element,
  Active bus, etc.
The interfaces generally point to the active object
  To work with another object, change the active object
    There are methods for selecting objects
    You may also use script commands

## Slide 104: DSS Interface
This is the main interface. It is instantiated upon loading OpenDSSEngine.DSS and then instantiates all other interfaces internally
Call the Start(0) method to initialize the DSS
DSS Class Functions (methods) and Properties

## Slide 105: A Simple VBA Macro (Class Exercise)
To run the IEEE 123-bus Test Feeder and plot the voltage profile

## Slide 106
Option Explicit
Public MyOpenDSS As OpenDSSengine.DSS
Public MyText As OpenDSSengine.Text
Public MyCircuit As OpenDSSengine.Circuit
Public Sub MyMacro()
Set MyOpenDSS = New OpenDSSengine.DSS
MyOpenDSS.Start (0)
Set MyText = MyOpenDSS.Text
Set MyCircuit = MyOpenDSS.ActiveCircuit
MyText.Command = "Compile (C:\OpenDSS\IEEETestCases\123Bus\IEEE123Master.dss)"
MyText.Command = "New Energymeter.M1 element=Line.L115 terminal=1"
MyText.Command = "Solve"
Dim MyVoltages As Variant
Dim MyNames As Variant
Dim Mydistances As Variant
MyVoltages = MyCircuit.AllBusVmagPu
MyNames = MyCircuit.AllNodeNames
Mydistances = MyCircuit.AllNodeDistances
Dim i As Integer, irow As Integer
irow = 1
For i = LBound(MyVoltages) To UBound(MyVoltages)
ActiveSheet.Cells(irow, 1).Value = MyNames(i)
ActiveSheet.Cells(irow, 2).Value = Mydistances(i)
ActiveSheet.Cells(irow, 3).Value = MyVoltages(i)
irow = irow + 1
Next I
Set MyOpenDSS = Nothing
End Sub

## Slide 107: Steps Required to Do This
Register OpenDSSEngine.DLL (32-bit)
Start Microsoft Excel
Type alt-F11 to open VBA editor
  Or Tools>Macro …
Select OpenDSS Engine under Tools>References
Insert>Module
Enter the VBA code into blank module
  Use correct path name for your computer
Execute the macro “MyMacro”

## Slide 108: Resulting Chart in Excel

## Slide 109: VBA Example
Option Explicit
Public DSSobj As OpenDSSengine.DSS
Public DSSText As OpenDSSengine.Text
Public DSSCircuit As OpenDSSengine.Circuit
Public Sub StartDSS()
' Create a new instance of the DSS
Set DSSobj = New OpenDSSengine.DSS
' Assign a variable to the Text interface for easier access
Set DSSText = DSSobj.Text
' Start the DSS
If Not DSSobj.Start(0) Then MsgBox "DSS Failed to Start"
End Sub
This routine instantiates the DSS and starts it. It is also a good idea at this time to assign the text interface variable.
Define some public variables that are used throughout the project

## Slide 110: VBA Example
Public Sub LoadCircuit(fname As String)
' Always a good idea to clear the DSS when loading a new circuit
DSSText.Command = "clear"
' Compile the script in the file listed under "fname" cell on the main form
DSSText.Command = "compile " + fname
' The Compile command sets the current directory the that of the file
' Thats where all the result files will end up.
' Assign a variable to the Circuit interface for easier access
Set DSSCircuit = DSSobj.ActiveCircuit
End Sub
This subroutine loads the circuit from the base script files using the Compile command through the Text interface. “fname” is a string contains the name of the master file.
There is an active circuit now, so assign the DSSCircuit variable.

## Slide 111: VBA Example
Public Sub LoadSeqVoltages()
' This Sub loads the sequence voltages onto Sheet1 starting in Row 2
Dim DSSBus As OpenDSSengine.Bus
Dim iRow As Long, iCol As Long, i As Long, j As Long
Dim V As Variant
Dim WorkingSheet As Worksheet
Set WorkingSheet = Sheet1 'set to Sheet1 (target sheet)
iRow = 2
For i = 1 To DSSCircuit.NumBuses ' Cycle through all buses
Set DSSBus = DSSCircuit.Buses(i) ' Set ith bus active
' Bus name goes into Column 1
WorkingSheet.Cells(iRow, 1).Value = DSSCircuit.ActiveBus.Name
' Load sequence voltage magnitudes of active bus into variant array
V = DSSBus.SeqVoltages
' Put the variant array values into Cells
' Use Lbound and UBound because you don't know the actual range
iCol = 2
For j = LBound(V) To UBound(V)
WorkingSheet.Cells(iRow, iCol).Value = V(j)
iCol = iCol + 1
Next j
iRow = iRow + 1
Next i
End Sub
This Sub puts the sequence voltage onto a spreadsheet
Define a variant to pick up the arrays
Cycle through all the buses
Get the bus name
Get the voltages into the variant array
Put them on the spreadsheet
Define a variable for the Bus interface

## Slide 112: Harmonic Solution

## Slide 113: Solving for Harmonic Flows
The OpenDSS solution algorithm heritage
    McGraw-Edison Steady-State Analysis Program (MESSAP) 1977-78
    McGraw-Edison Harmonic Analysis Program (MEHAP) 1979-1982
    McGraw/Cooper V-Harm® program (1984)
    Electrotek Concepts SuperHarm® program (1990-92)
    Electrotek DSS (1997)
Harmonic solution has been an integral part of the program since its inception

## Slide 114: Harmonic Solution
All Load elements have ‘Spectrum=default’
  The default spectrum is a typical 3-phase ASD spectrum
  Re-define Spectrum.Default if you want something else
    Edit spectrum.default …
    Or create a new Spectrum and assign Loads to it
Harmonic solution requires a converged power flow solution to initialize all the harmonic sources
  Do “Solve mode=direct” if convergence is difficult to achieve

## Slide 115: Typical Harmonic Solution Script
Typical script for Harmonics Solution
  Solve ! Snapshot power flow
  Solve mode=harmonics
This will solve for all frequencies defined in the problem
  Make sure you have Monitors where you want to see results because results will come fast!
  Post process Monitor data in Excel, Matlab, etc. to compute THD, etc.

## Slide 116: Load Modeling for Harmonics Studies
Original Model
Present Model

## Slide 117: Transformer Modeling
There is now (7.6.3.14) an option to hold X/R Constant
  More appropriate for substation transformer
  Distribution transformers have lower X/R
Modeling with Reactor
Frequency dependence is coming … Here!
  R Curve (XYCurve object)
  L Curve

## Slide 118: What Difference Does it Make?

## Slide 119: Harmonic Solution Mode
Solve the power flow (fundamental frequency)
Harmonic current sources in LOAD models are initialized to match the fundamental frequency solution
Generators converted to Thevenin voltage behind Xd”
“Solve Mode=Harmonics”
  Program solves at each frequency that is defined
  Non-iterative (direct solution)
  Harmonic currents assumed invariant
  Y matrix is rebuilt for each frequency
  Need MONITOR objects to capture results

## Slide 120: Harmonic Solution Mode, Cont’d
Frequency Scans
  Define a scan spectrum at a small frequency increment
  Assign it to an ISOURCE or VSOURCE
  You probably want do disable LOAD and GENERATOR harmonic spectra, e.g.:
    Spectrum.DefaultLoad.NumHarm=1
    Otherwise, LOAD objects will inject a current at integer harmonic frequencies yielding a really weird solution
  Scans can be performed for (see ScanType property)
    Positive sequence
    Zero sequence
    No sequence
Example Frequency Scan
  …\Distrib\Examples\FreqScan folder

## Slide 121: Frequency Scan Example Script
// THIS SCRIPT WILL RUN A FREQUENCY SCAN ON THE IEEE 123 BUS TEST CASE
Spectrum.DefaultLoad.NumHarm=1 ! This effectively gets rid of LOAD harmonics
// Define a spectrum for the scan source
New spectrum.Scanspec numharm=1000 csvfile=ScanSpectrum.csv
// Put a Monitor to capture the results
New Monitor.Mscan Line.l84 1
// Define a positive-sequence (the default) 1-A, 3-ph current source
New Isource.scansource bus1=83 amps=1 spectrum=scanspec
solve ! solve the power flow at fundamental
solve mode=harmonics ! do the harmonic solutions
show mon mscan ! show the results
Export monitors mscan
// You can plot the Monitor, but Excel or Matlab might be better
Plot monitor object= mscan channels=(1 3 5 )

## Slide 122: What Does the Scan Spectrum Look Like?
1.083333333 100 0
1.166666667 100 0
1.25 100 0
1.333333333 100 0
1.416666667 100 0
1.5 100 0
1.583333333 100 0
1.666666667 100 0
1.75 100 0
1.833333333 100 0
1.916666667 100 0
2 100 0
2.083333333 100 0
2.166666667 100 0
2.25 100 0
2.333333333 100 0
2.416666667 100 0
2.5 100 0
2.583333333 100 0
… etc …
For 60 Hz base frequency, this gives a 5 Hz scan
Harmonic
% Magnitude
(All 100%)
Phase Angle
(All 0)
This is typically associated with a 1-A current source, so that the resulting voltages represent driving-point Z, transfer Z, etc.

## Slide 123: What Difference Does it Make?

## Slide 124: Putting it All Together - Harmonics
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements, each frequency
PC Elements Harmonic injection Currents
V
Node
Voltages
(each Frequency)

## Slide 125: Dynamics Solution

## Slide 126: Dynamics Mode
Dynamics mode is used for
  Fault current calculations including Generator contributions
    Single time-step solution
  Machine transients
  Inverter transients
Typical time step: 0.2 – 1 ms
  Depends on time constants in model
A converged power flow is required to initialize the model.

## Slide 127: Basic Algorithm (From SolutionAlgs.Pas)
Increment_time;
{Predictor}
IterationFlag := 0;
IntegratePCStates;
SolveSnap;
{Corrector}
IterationFlag := 1;
IntegratePCStates;
SolveSnap;

## Slide 128: Entering Dynamics Mode
Initialize state variables in all PC Elements
  For example, in a Generator object currently:
    Compute voltage, E1, behind Xd‘ and Initialize the phase angle, , to match power flow (approximately)
Set derivatives of the state variables to zero
  For the Generator: Speed (relative to synch frequency), Angle
Set controlmode=time
  When running in time steps of a few seconds or less, controls that depend on the control queue for instructions on delayed actions will be automatically sequenced when the solution time reaches the designated time for an action to occur.

## Slide 129: 3-Phase Generator Model in Dynamics Mode
E

## Slide 130: Differential Equations for Default Generator (1-Mass)
Derivative Calculation:
Integration
Trapezoidal integration formula for , for example:

## Slide 131: User-Written DLLs
More complex behaviors can be modeled using Dynamic-Linked Libraries
Requires more sophisticated programming skills
Certain PCElements provide interfaces
  Some Control elements, too
There is some documentation in the Doc folder, but it is limited
IndMach012 is an example supplied with the program
  A symmetrical component based induction machine model for the Generator class element

## Slide 132: Running from MATLAB

## Slide 133: Running OpenDSS From Matlab
Starting the DSS
function [Start,Obj,Text] = DSSStartup
% Function for starting up the DSS
%
%instantiate the DSS Object
Obj = actxserver('OpenDSSEngine.DSS');
%
%Start the DSS. Only needs to be executed the first time w/in a
%Matlab session
Start = Obj.Start(0);
% Define the text interface to return
Text = Obj.Text;
%Start up the DSS
[DSSStartOK, DSSObj, DSSText] = DSSStartup;

## Slide 134: Using the DSS through the Text Interface from Matlab (harmonics example)
%Compile the DSS circuit script
DSSText.Command = 'compile master.dss';
% get an interface to the active circuit called "DSSCircuit"
DSSCircuit = DSSObj.ActiveCircuit;
%Determine which connection type for the source and call
%appropriate DSS file
switch XFMRType
case 1
DSSText.Command = 'redirect directconnectsource.DSS';
case 2
DSSText.Command = 'redirect deltadelta.DSS';
case 3
DSSText.Command = 'redirect deltawye.DSS';
otherwise
disp('Unknown source Connection Type')
end
%Set the system frequency and vsource frequency for harmonic requested
DSSText.Command = ['set frequency=(' num2str(Freq) ' 60 *)'];
DSSText.Command = ['vsource.source.frequency=(' num2str(Freq) ' 60 *)'];

## Slide 135: Using the DSS through the Text Interface from Matlab (harmonics example) (cont’d)
% Vary the parameters according to a random distribution
% If more parameters need to be varied, just add them to the below
% list. Set ParamNum to total number of parameters varied
ParamNum = 6; %ParamNum used for sorting/plotting
for Case_Count = 1:Max_Cases
%Create index in the OutputData matrix to keep the cases in order
OutputData(Case_Count,1) = Case_Count;
% Generate random new coordinates for each conductor
[x1 y1 x2 y2 x3 y3 geomean] = RandomGeometry(8,0.75,30);
(... etc. etc. )
%define a new line geometry with random spacing
DSSText.Command = ['New LineGeometry.OHMOD nconds=3 nphases=3 cond=1 wire=acsr336 x=' num2str(x1) ' ' num2str(y1) ' units=ft cond=2 wire=acsr336 x=' num2str(x2) ' ' num2str(y2) ' units=ft cond=3 wire=acsr336 x=' num2str(x3) ' ' num2str(y3) ' units=ft'];
%Solve the circuit
DSSText.Command = 'solve';
(etc. etc.)

## Slide 136: Running with Python
See Python Example in Examples Folder …

## Slide 137: Invoking DSS on IEEE 123 Bus Case

## Slide 138: Python Example

## Slide 139: Running From C#
Using Visual Studio 2013 Express Version

## Slide 140: Create a New Visual C# Project …

## Slide 141: Select Project > Add Reference …

## Slide 142: Choose OpenDSSEngine from the List …

## Slide 143: Add “using” clause in Code View ..
You will get a helpful hint

## Slide 144: Add Public Variable for DSS object
Type is DSS (the editor will prompt you when you start to type it)
This is the main interface to OpenDSSEngine. The registered interface is “OpenDSSEngine.DSS”

## Slide 145: From ToolBox, add a Button the Main Form to Load and Start OpenDSS
Double-Click this to create code for processing button click
Set the Text property of the button control to “Start &OpenDSS”

## Slide 146: Start OpenDSS and Check if OK
Add public variable for Text interface after OpenDSS starts OK
This is the code generated to handle the button click (named StartButton)
This connects DSSObj variable to the COM server and loads the server
Attempt to start the OpenDSS program
If successful, assign the variable for the Text interface

## Slide 147: Test it --- Success!
Click Start
Then click this
Now we’re off and running!

## Slide 148: Solve the IEEE 123-Bus Test Feeder
Add some stuff to the main form
TextBox with full path name of the IEEE123Master.DSS file

## Slide 149: Start Button Code
No message on successful start
New Helper Variables
Set the new variables

## Slide 150: Compile Button Code
Sends Compile command to text interface
Contents of TextBox
Check Error Number on return
If error, show result message
Otherwise show “No Errors.”

## Slide 151: Solve Button Code
Invoke Solve method in Solution interface
Check for lack of convergence

## Slide 152: Show Results Button Code
Simply sends three commands to Text interface

## Slide 153: What Do You want to Do?
Add other functions to the app or do other C# demos …

## Slide 154: A Storage Modeling Example
OpenDSS STORAGE and STORAGECONTROLLER objects

## Slide 155: Storage Element Model in OpenDSS
% Eff. Charge/Discharge
Idle | Discharge | Charge
Idling Losses
kW, kvar
kWh STORED
Other Key Properties
% Reserve kWhRated kWhStored %Stored kWRated
etc.

## Slide 156: StorageController Element in OpenDSS
Discharge Mode Charge Mode kW Target Discharge Time Total Fleet kW Capacity Total Fleet kWh
et. al.
Storage “Fleet”
Substation
V, I
Comm Link
Time + Discharge rate Peak Shaving Load Following Loadshape

## Slide 157: Simple Peak Shave Example – 75 kWh ea.

## Slide 158: Simple Peak Shave Example – 25 kWh ea.
“Ran Out of Gas”

## Slide 159: Simple Storage Script Using a DynaDLL
Clear
New Circuit.SimpleStore ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.02 ISC3=30000 ISC1=25000 !Define source V and Z
New Transformer.TR1 XHL=10
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[200000 200000]
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=0.011 Units=Mi
New Transformer.MVLV XHL = 5
~ Buses=[LoadBus LVBus]
~ Conns=[Delta Wye]
~ kVs= [12.47 .400]
~ kVAs=[300 300]
New Storage.Store1 phases=3 Bus1=LVBus kV=0.400 conn=Delta kVA=60
~ kWrated=60 kWHrated= 0.20833 %reserve=50 // 750 kW-s (kJ)
~ state=discharge
~ kW=50 PF=1
~ DynaDLL="C:\Users\prdu001\OpenDSS\Source\DESS1\Dess1.DLL"
~ DynaData=(file=DESSModel_Test.Txt)
// New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95 model=4 cvrwatts=1.2
Solve

## Slide 160: Defining a StorageController
Compile Master.DSS
Redirect AllocateLoadsandMeters.DSS
BusCoords colfax21_EXP_BUSCOORDS.CSV
BusCoords buscoordsCES.DSS ! COORDINATES OF CES LOCATIONS
Set maxcontroliter=20
! ****** ADD STORAGE, SET TO DISCHARGE AND SOLVE ***************************
redirect CES.DSS
! define storage controller
! discharge = load follow ! charge=time
New StorageController.CESmain element=line.568_4921721 terminal=1
~ kWTarget=8000 PFTarget=0.98 %ratecharge=30
~ eventlog=y
New monitor.Store Storage.jo0211000173 1 mode=1 ppolar=no
New monitor.StoreVars Storage.jo0211000173 1 mode=3
solve
Define basic circuit
Define Storage Fleet
Fleet Controller Default Peakshave Mode @ 8 MW

## Slide 161: Snippet of CES.DSS File Defining Storage Fleet
New storage.JO0235001304 phases=1 bus1=X_68_4921721_JO0235001304.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000257 phases=1 bus1=X_68_4921721_JO0235001304.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000265 phases=1 bus1=X_43_4921721_JO0235000258.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000268_1 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000268_2 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000269_1 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000269_2 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000272_1 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000272_2 phases=1 bus1=X_608_4921721_JO0235000273.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000274 phases=1 bus1=X_611_4921721_JO0235000274.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000583 phases=1 bus1=X_111_4921721_JO0235000585.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235001512 phases=1 bus1=X_470_4921721_JO0235000552.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000618 phases=1 bus1=X_637_4921721_JO0235000563.1 yearly=Phasealoadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
New storage.JO0235000593 phases=1 bus1=X_526_4921721_JO0235000559.3 yearly=Phasecloadshape kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
- - - - -
- - - - -

## Slide 162: Introduction to OpenDSS Internals
How it works. A tour of the source code. A look at DLL interfaces.

## Slide 163: DSS Object Structure
DSS Executive
Circuit
PDElement
PCElement
Controls
Meters
General
Line Transformer Capacitor Reactor
Load Generator Vsource Isource Storage
…
RegControl CapControl Relay Reclose Fuse
Monitor EnergyMeter Sensor
LineCode LineGeometry WireData LoadShape GrowthShape Spectrum TCCcurve XfmrCode
Commands
Options
Solution
V
[Y]
I

## Slide 164: DSS Class Structure
Instances of Objects of this class
Property Definitions
Class Property Editor
Collection Manager
Class
Object 1
Property Values
Methods
Yprim
States
Object n
Property Values
Methods
Yprim
States

## Slide 165: Solution Object (Solution.pas)
TNodeVarray = Array[0..1000] of Complex;
pNodeVarray = ^TNodeVarray;
TSolutionObj = class(TDSSObject)
private
dV :pNodeVArray; // Array of delta V for Newton iteration
FFrequency:Double;
FUNCTION Converged:Boolean;
FUNCTION OK_for_Dynamics(const Value:Integer):Boolean;
FUNCTION OK_for_Harmonics(const Value:Integer):Boolean;
Function SolveSystem(V:pNodeVArray):Integer;
PROCEDURE AddInAuxCurrents(SolveType:Integer);
PROCEDURE DoNewtonSolution;
PROCEDURE DoNormalSolution;
PROCEDURE GetPCInjCurr;
PROCEDURE GetSourceInjCurrents;
procedure Set_Frequency(const Value: Double);
PROCEDURE Set_Mode(const Value: Integer);
procedure Set_Year(const Value: Integer);
PROCEDURE SetGeneratordQdV;
PROCEDURE SumAllCurrents;
PROCEDURE ZeroInjCurr;
public
Algorithm :Integer; // NORMALSOLVE or NEWTONSOLVE
AuxCurrents :pComplexArray; // For injections like AutoAdd
ControlActionsDone :Boolean;
ControlIteration :Integer;
ControlMode :Integer; // EVENTDRIVEN, TIMEDRIVEN
ConvergenceTolerance :Double;
ConvergedFlag:Boolean;
DefaultControlMode :Integer; // EVENTDRIVEN, TIMEDRIVEN
DefaultLoadModel :Integer; // 1=POWERFLOW 2=ADMITTANCE
DoAllHarmonics : Boolean;
DynamicsAllowed :Boolean;
DynaVars:TDynamicsRec;
ErrorSaved :pDoubleArray;
FirstIteration :Boolean;
FrequencyChanged:Boolean; // Flag set to true if something has altered the frequency
Fyear :Integer;
Harmonic :Double;
HarmonicList :pDoubleArray;
HarmonicListSize :Integer;
hYsystem :LongWord; {Handle for main (system) Y matrix}
hYseries :LongWord; {Handle for series Y matrix}
hY :LongWord; {either hYsystem or hYseries}
IntervalHrs:Double; // Solution interval since last solution, hrs.

## Slide 166: Solution Object – Key Variables
IsDynamicModel :Boolean;
IsHarmonicModel :Boolean;
Iteration :Integer;
LoadModel :Integer; // 1=POWERFLOW 2=ADMITTANCE
LastSolutionWasDirect :Boolean;
LoadsNeedUpdating :Boolean;
MaxControlIterations :Integer;
MaxError :Double;
MaxIterations :Integer;
MostIterationsDone :Integer;
NodeVbase :pDoubleArray;
NumberOfTimes :Integer; // Number of times to solve
PreserveNodeVoltages:Boolean;
RandomType :Integer; //0 = none; 1 = gaussian; 2 = UNIFORM
SeriesYInvalid :Boolean;
SolutionCount :Integer; // Counter incremented for each solution
SolutionInitialized :Boolean;
SystemYChanged :Boolean;
UseAuxCurrents :Boolean;
VmagSaved :pDoubleArray;
VoltageBaseChanged :Boolean;
{Voltage and Current Arrays}
NodeV :pNodeVArray; // Main System Voltage Array
allows NodeV^[0]=0
Currents :pNodeVArray; // Main System Currents Array

## Slide 167: Solution Object -- Public Functions and Properties
PROCEDURE ZeroAuxCurrents;
FUNCTION SolveZeroLoadSnapShot :Integer;
PROCEDURE DoPFLOWsolution;
PROCEDURE Solve; // Main Solution dispatch
PROCEDURE SnapShotInit;
FUNCTION SolveSnap:Integer; // solve for now once
FUNCTION SolveDirect:Integer; // solve for now once, direct solution
FUNCTION SolveYDirect:Integer; // Similar to SolveDirect; used for initialization
FUNCTION SolveCircuit:Integer; // SolveSnap sans control iteration
PROCEDURE CheckControls; // Snapshot checks with matrix rebuild
PROCEDURE SampleControlDevices;
PROCEDURE DoControlActions;
PROCEDURE Sample_DoControlActions; // Sample and Do
PROCEDURE Check_Fault_Status;
PROCEDURE SetGeneratorDispRef;
PROCEDURE SetVoltageBases;
PROCEDURE SaveVoltages;
PROCEDURE UpdateVBus; // updates voltages for each bus from NodeV
PROCEDURE RestoreNodeVfromVbus; // opposite of updatebus
FUNCTION VDiff(i,j:Integer):Complex; // Difference between two node voltages
PROCEDURE InitPropertyValues(ArrayOffset:Integer);Override;
PROCEDURE DumpProperties(Var F:TextFile; Complete:Boolean); Override;
PROCEDURE WriteConvergenceReport(const Fname:String);
PROCEDURE Update_dblHour;
PROCEDURE Increment_time;
// set the Mode
Property Mode :Integer Read dynavars.SolutionMode Write Set_Mode;
// Solution Frequency
Property Frequency :Double Read FFrequency Write Set_Frequency;
// Year for multiyear solutions
Property Year :Integer Read FYear Write Set_Year;

## Slide 168: Adding a New Model
Create a Delphi unit (.pas file) with a unique name for example MyModel.
Use an existing unit as a pattern.
  Collection manager of class TMyModel
    Has class Edit function
    Assigns the Class_Name variable = ‘MyModel’
  Object model of class TmModelObj
Add MyModel to the Uses clause of DSSClassDefs.pas
Add a statement to Create the class:
  DSSClasses.New := TMyModel.Create;
OpenDSS now recognizes the class and will pass property definition strings to the Edit function to process

## Slide 169: The Edit Function
When you write this script:
  New MyModel.ThisInstance phases=3 kV=100 …
This makes a new instance of the objects and invokes the MyModel Edit Function
Everything out here is passed to the MyModel Edit function
(The Edit command tries to find an existing instance of this class of object)

## Slide 170: The Edit Function
The author of the model can write whatever code he/she chooses to process the property data.
The standard models use the CASE statement and “TCommandList” class to process properties
  In the base “TDSSClass” and is part of all objects
  Write the DefineProperties procedure
    Use an existing element such as Capacitor as a pattern
    You can add properties as you see fit
    Define PropertyHelp array so help string will automatically show up in the Help menu
Note: The Edit function operates on the Active element

## Slide 171: The Edit Function
VAR
ParamPointer:Integer;
ParamName:String;
Param:String;
BEGIN
Result := 0;
// continue parsing with contents of Parser
ActiveCapacitorObj := ElementList.Active;
ActiveCircuit.ActiveCktElement := ActiveCapacitorObj; // use property to set this value
WITH ActiveCapacitorObj DO BEGIN
ParamPointer := 0;
ParamName := Parser.NextParam;
Param := Parser.StrValue;
WHILE Length(Param)>0 DO BEGIN
IF Length(ParamName) = 0 THEN Inc(ParamPointer)
ELSE ParamPointer := CommandList.GetCommand(ParamName);
If (ParamPointer>0) and (ParamPointer<=NumProperties)
Then PropertyValue[ParamPointer]:= Param;
ParamName := Parser.NextParam;
Param := Parser.StrValue;
END;
CASE ParamPointer OF
0: DoSimpleMsg('Unknown parameter "'+ParamName+'" for Object "Capacitor.'+Name+'"', 450);
1: CapSetbus1(param);
2: Setbus(2, param);
3:{ Numphases := Parser.IntValue}; // see below
4: InterpretDblArray (Param, FNumSteps, FkvarRating);
5: kvRating := Parser.Dblvalue;
… etc…
ELSE
// Inherited Property Edits
ClassEdit(ActiveCapacitorObj, ParamPointer - NumPropsThisClass)
END;
Main Case Statement Processes Each Property
Iterate through property names found on script line

## Slide 172: Command and Option Processing
Commands and Options are processed using the same technique as the Edit function
The CASE statement format is used throughout the program
All commands are implemented in text in this manner first
This structure allows new commands and options to be added without disturbing the rest of the program
Likewise, new properties can be added to device models without much fear of breaking previous properties

## Slide 173: Basic Functions in a Device Model (Required)
DefineProperties
MakeLike
Create/Destroy constructors/destructors
Edit
Init
NewObject
RecalcElementData
CalcYPrim (for PC and PD elements)
InitPropertyValues
GetPropertyValue (important for editing and displays)
DumpProperties

## Slide 174: Classes in a Device Model
TMyModel
  Support for Edit function
  Define properties, manage collection
TMyModelObj
  Private Data and various functions
    State variable, parameter values
    Local module functions
  Public
    Variables needed by other modules
    Property definitions for accessing private data
    Required Functions/Procedures

## Slide 175: Together... Shaping the Future of Electricity
(The End)