## Slide 1: Advanced Modeling for Distribution Planning Workshop with OpenDSS
Instructors
Roger C. Dugan Matt Rylander
Sponsored by CenterPoint Energy At Texas A&M University April 19, 20, 21

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Instructor
Matthew Rylander Technical Leader Power Systems Studies Power Delivery and Utilization mrylander@epri.com (512) 351-9938
Matthew Rylander is a Technical Lead Engineer at the Electric Power Research Institute. His current research activities focus on transmission and distribution system issues such as analyzing operational strategies to improve system operation and evaluating the impact of distributed resources. Before joining EPRI, Matthew received his Doctorate from the University of Texas at Austin in 2008 and worked at the Electric Reliability Council of Texas.
Area of Responsibility – Distribution System Analysis and the Integration of Distributed Energy Resources
The past 5 years have been spent in detailed distributed energy resource (DER) analysis to the distribution system. The detailed analysis have examined DER impact methods from screening, clustering, and more streamlined techniques. Those analyses have also led to the impacts considering hosting capacity, operational flexibility, smart inverter settings, power quality aspects, and the values of DER.
Recent Publications & Research Results
Integration of Hosting Capacity Analysis into Distribution Planning Tools. EPRI, Palo Alto, CA: 2015. 3002005793.
Analysis to Inform CA Grid Integration: Methods and Default Settings to Effectively Use Advanced Inverter Functions in the Distribution System. EPRI, Palo Alto, CA: 2015. 3002007139.
Alternatives to the 15% Rule: Modified Screens and Validation. EPRI, Palo Alto, CA: 2015. 3002005791.

## Slide 4: Introduction to Distribution Systems

## Slide 5: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 6: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 7: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 8: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 9: Urban Low-Voltage Network Systems

## Slide 10: Urban LV Network Systems – Another View
SUBSTATION
TRANSMISSION
SYSTEM
FEEDER BREAKER
OR RECLOSER
LOW-VOLTAGE NETWORK
NETWORK
PROTECTOR
PRIMARY FEEDERS

## Slide 11: Urban LV Network Systems
Used in downtown areas (e.g., Manhattan) requiring extraordinary reliability
In a number of major cities
  New York
  Seattle
  Chicago
Reliability is on the order of 100 times better than radial
Much more costly to build
Use devices not found on other distribution systems
  Network transformer and network protectors
Most distribution systems in the world are radial

## Slide 12: Why are most distribution systems radial?

## Slide 13: Utility Fault-Clearing Practices
  This explains why most systems are radial
Important to understand this for DER application on the “Integrated Grid”
  Lower-cost protection for the inevitable short circuit
This is where many of the operating conflicts arise !!
DER response during faults can
  Affect utility practices, fault clearing
  Be damaged by fault clearing practices

## Slide 14: The Fuse Characteristic Dictates Utility Fault Protection Practices On Distribution

## Slide 15: Fuse Characteristic, cont’d
A fuse is a one-shot device
Operates faster for higher currents
To coordinate with this:
  Upstream devices have same basic shape
  Devices closer to substation act slower
    Except for “fast” or “instantaneous” tripping where we try once or twice to save the fuse

## Slide 16: Radial Distribution Fault Protection
Series Overcurrent Devices
Only one device operates to clear fault
(current is expected from only one source)

## Slide 17: Transmission Fault Protection
Multiple Sources
Two Devices Must Operate to Clear Fault

## Slide 18: Radial Circuit Economics
Most distribution systems are radially configured because the protection system is
  Simpler to operate
  Less expensive to build
Smart, or “Integrated”, Grid with multiple sources in changing that
  Current flows in more than one direction
  Overcurrent relaying/fuses inadequate on microgrids

## Slide 19: Radial System Protection Principles
Radial Distribution Systems are employed because protection is economical
DER provides multiple sources for faults
System must revert to radial configuration for the fault clearing to proceed when using conventional radial system overcurrent protection.

## Slide 20: LV Network Systems

## Slide 21: LV Network Protection Principles
Designed for higher reliability than a radial system
  Can withstand more failures (2 or more)
Network protectors open very quickly on reverse power
  Assumption: The only time the power will reverse is for a fault
  Have to shut off all sources of fault current
  This makes it very difficult to accommodate much DER on urban LV networks

## Slide 22: Reclosing on Radial Circuits
Most faults on primary distribution are temporary
  Lightning
  Trees blow into lines
Reclosing allows for prompt restoration of service
  Interrupt current and allow arc to disperse
  Automatically reclose to restore service
Very common on North American distribution systems

## Slide 23: Typical Reclosing Sequences
DG may prevent faults from clearing
DG may be damaged by reclose
DG must disconnect here

## Slide 24: Summary: Distribution Systems
Structure and operations are dictated by the economics of the protection system and desired Reliability
It will be too costly to modify the protection system just to accommodate DER devices
DER must disconnect for fault clearing on same feeder or LV network
The greater value for DER is generally on the end-user side or to subtransmission feed to distribution
DER can economically defer investments in distribution infrastructure under some circumstances

## Slide 25: Introduction to the OpenDSS Program

## Slide 26: What is the OpenDSS?
Many of the examples in this course will be taught using the EPRI OpenDSS computer program
The program is freely available and is updated regularly
You may find it on www.Sourceforge.net
Also, bookmark the EPRI link site:
  http://smartgrid.epri.com/SimulationTool.aspx

## Slide 27: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    As well as European-style systems
      These typically have a simpler structure

## Slide 28: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation
DG
  Interconnection studies/screening
  Value of service studies (risk based)
  Solar PV voltage rise/fluctuation
  Wind power variations impact
  Hi-penetration solar PV impacts
  Harmonic distortion
  Dynamics/islanding

## Slide 29: What can OpenDSS be used for? (cont’d)
Hybrid simulation of communications and power networks
Geomagnetically-Induced Current (GIC) flow (solar storms)
Power delivery loss evaluations (EPRI Green circuits program - > 80 feeders)
Voltage optimization
PEV/PHEV impact simulations
Community energy storage (EPRI Smart Grid Demo)
High-frequency harmonic/interharmonic interference
Various unusual transformer configurations
Transformer frequency response analysis
Distribution automation control algorithm assessment
Impact of tankless electric water heaters
Wind farm collector simulations
Wind farm interaction with transmission
Wind generation impact on capacitor switching and regulator/LTC tapchanger operations
Protection system simulation
Open-conductor fault conditions
Circulating currents on transmission skywires
Ground voltage rise during faults on lines
Stray voltage simulations
Industrial load harmonics studies/filter design
Distribution feeder harmonics analysis, triplen harmonic filter design
And many more ….

## Slide 30: Some Examples

## Slide 31: Computing Annual Losses
Peak load losses are not necessarily indicative of annual losses

## Slide 32: Using DSS to Determine Incremental Capacity of DG
“How much more power can be served at the same risk of unserved energy?”
Broad Summer Peaking System
“Needle” Peaking System

## Slide 33: DG Dispatch

## Slide 34: Solar PV Simulation

## Slide 35: 1-sec Solar Data – Cloud Transients
Impact on Feeder Voltage

## Slide 36: 1-sec Solar PV Simulation Shows Voltage Regulation Issues
Regulator Operations

## Slide 37: Power Distribution Efficiency
Light Load Week
Peak Load Week

## Slide 38: Wind Plant 1-s Simulation
Notes: The plot you see to the right is a sample case study we did where a developer wanted to install 3 750kW turbines at the end of a 10-mile distribution feeder. Along the feeder was a voltage regulator and large intermittent load. The concern we had was the impact the turbine output fluctuations would have on the flicker, regulator action, as well as the voltage profile along the feeder. Utilizing software that Electrotek had developed, specifically the Distribution System Simulator, or DSS,, minor modifications were made that allowed us to simulate the wind plant fluctuation impact over time, thus giving us the ability to address the concerns at hand.
The plot you see to the right is simulation output from the DSS, over a time horizon of ~ 4 minutes. The three turbines were modeled explicitly, along with the 5-step switched capacitor banks connected to each turbine as well as the voltage regulator upline from the wind plant. This software allows us to make recommendations to the utility and/or wind plant developer regarding modifications necessary, if any, to allow for the wind plant to have minimal impact on the distribution feeder and surrounding customers, or perhaps even improve feeder performance.
We also utilize this software for estimating flicker according the IEC standard 1400-21. The software, along with data specific to the turbine being considered allows one to estimate the flicker impact BEFORE the turbine is installed.

## Slide 39
Broadband Driving Point Admittance
0
0.005
0.01
0.015
0.02
0.025
0.03
0.035
0
100000
200000
300000
400000
500000
Frequency, Hz
Siemens
|Y|

## Slide 40: Power Flow Visualization

## Slide 41: Special Displays
Fault Current Magnitudes

## Slide 42: Example of an Expected DG Problem
Regulator taps up to compensate for voltage drop
Voltage overshoots as power output ramps up

## Slide 43: Root of Problem
Voltage Profile w/ DG
0.0
2.0
4.0
6.0
Distance from Substation (km)
0.90
0.95
1.00
1.05
1.10
p.u. Voltage
High Voltages
Distribution Systems designed for voltage DROP, not voltage RISE.

## Slide 44: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose: DG interconnection analysis

## Slide 45: What is the OpenDSS? (cont’d)
What it Isn’t
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a Power Flow program
  Not a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 46: Time- and Location-Dependent Benefits
The OpenDSS was designed to capture both
  Time-specific benefits and
  Location-specific benefits
Needed for
  DG analysis
  Renewable generation
  Energy efficiency analysis
  PHEV and EV impacts
  Other proposed capacity enhancements that don’t follow typical loadshapes

## Slide 47: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak loading conditions
  Capture mostly location-specific benefits
  Ignores time; Assumes resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do time sequence analysis to get the right answer
  Over distribution planning area

## Slide 48: What are the Key Features?
See Documentation for more details
  http://svn.code.sf.net/p/electricdss/code/trunk/Distrib/Doc/
Designed to allow expansion indefinitely
  Impossible to anticipate everything users will want to do
  Scripting language and COM interface allows easier customization

## Slide 49: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 50: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 51: Overall Model Concept

## Slide 52: User Interfaces Currently Implemented
A stand-alone executable program that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  (An out-of-process COM server is under development to support execution from 64-bit programs.)
A direct DLL interface that mimics the COM interface
  For non-Windows platforms, such as HPCs
  For programming languages that do not support COM or are not efficient at supporting COM

## Slide 53: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, Synergi, and WindMil programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders (OpenDSS versions installed with the program)
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Used to develop the DG Protection test feeder and the YDY test case
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data.
Calibrated against measurements on feeders with 100% AMI

## Slide 54: Needs Envisioned by EPRI for the Smart Grid (2007)
Sequential time simulation (QSTS)
Meshed network solution capability
Better modeling of Smart Grid controllers
Advanced load and generation modeling
High phase order modeling ( >3 phases)
  Stray voltage (NEV), crowded ROWs, etc.
Integrated harmonics
  NEV requires 1st and 3rd
User-defined (scriptable) behavior
Dynamics for DG evaluations
= Original Capabilities in 1997

## Slide 55: EPRI’s Vision
Distribution planning and distribution management systems (DMS) will converge
  Into a unified set of analysis tools.
Real-time analysis and planning analysis will merge into common tools.
Distribution system analysis tools will continue to play an important role,
  Although they might appear in a much different form than today.

## Slide 56: Plan for Future Work/Enhancements
We plan to exploit high performance desktop computing to make it feasible to study distribution systems of at least 100,000 nodes and perhaps as many as 1,000,000 nodes.
  OpenDSS-PM (for Parallel Machine) developed in 2016 to perform parallel processing for faster QSTS simulations
  Can solve different time periods in parallel
  Employs Diakoptics to solve very large networks
  Still under development with US DOE (Sandia & NREL) contract (since 2016)
Improved distribution state estimation functions
Improved microgrid simulations (Dynamics mode)
Improved Distribution Management Systems (DMS) functions
  Existing EPRI research project

## Slide 57: What’s Next?
Other Advanced Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”

## Slide 58: Getting Started: Installation and Basic Usage

## Slide 59: Repository on SourceForge.Net

## Slide 60: Accessing the SourceForge.Net Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from Tortoisesvn.net/downloads.
Recommendation:
  Then, to grab the files from SourceForge by: 1 - create a clean directory such as "c:\opendss" 2 - right-click on it and choose "SVN Checkout..." from the menu 3 - the repository URL is
    http://electricdss.svn.sourceforge.net/svnroot/electricdss
    (Change the checkout directory if it points somewhere other than what you want.)
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 61: Program Installation

## Slide 62: Download the Installer Files

## Slide 63: Install Both 32-bit and 64-bit Versions of OpenDSS
DG Screener and Excel typically use 32-bit OpenDSS, but both versions must be installed to get 32-bit server fully installed. Windows will figure out which one needs to be executed. Magic!!

## Slide 64: OpenDSS Files Installed
Main Program Files

## Slide 65: SourceForge.Net Links for OpenDSS
EPRI Links Page
  http://smartgrid.epri.com/SimulationTool.aspx
OpenDSS Download Files:
  http://sourceforge.net/projects/electricdss/files/
Top level of Main Repository

## Slide 66: Discussion Forum & News for OpenDSS

## Slide 67: EPRI OpenDSS Link Page
    http://smartgrid.epri.com/SimulationTool.aspx

## Slide 68: Registering the COM server
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 69: The GUID References the DLL File ….
If you look up the GUID in RegEdit
Points to OpenDSSEngine.DLL (In-process server, Apartment Threading model)

## Slide 70: Questions So Far?

## Slide 71: OpenDSS Architecture and Circuit Modeling Basics
.

## Slide 72: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs

## Slide 73: DSS Object Structure
DSS Executive
Circuit
PDElement
PCElement
Controls
Meters
General
Line Transformer Capacitor Reactor
Load Generator Vsource Isource Storage
RegControl CapControl Relay Reclose Fuse
Monitor EnergyMeter Sensor
LineCode LineGeometry WireData LoadShape GrowthShape Spectrum TCCcurve XfmrCode
Commands
Options
Solution
V
[Y]
I

## Slide 74: DSS Class Structure
Instances of Objects of this class
Property Definitions
Class Property Editor
Collection Manager
Class
Object 1
Property Values
Methods
Yprim
States
Object n
Property Values
Methods
Yprim
States

## Slide 75: Models Currently Implemented (April 2017)
POWER DELIVERY ELEMENTS
  CAPACITOR (Series and shunt capacitors; filter banks)
  LINE (All types of lines, cables)
  REACTOR (Series and shunt reactors)
  TRANSFORMER (multi-phase, multi-winding transformer models)
POWER CONVERSION ELEMENTS
  GENERATOR (General generator models)
  LOAD (General load models)
  PVSYSTEM (Solar PV system with panel and inverter)
  STORAGE (Generic storage element models)
  INDMACH012 (Induction Machine Model in Symmetrical Components)
CONTROL ELEMENTS
  CAPCONTROL (Capacitor bank control; various types)
  FUSE (Controls a switch, modeling fuse TCC behavior)
  GENDISPATCHER (A specialized controller for dispatching DG)
  RECLOSER (Controls a switch, modeling recloser behavior)
  REGCONTROL (Standard 32-step regulator/LTC control)
  RELAY (Controls a switch, modeling various relay behaviors)
  STORAGECONTROLLER (Implementation of AEP’s hub controller)
  SWTCONTROL (one way to control switches during simulations)
  INVCONTROL (Inverter control for VVO, etc)

## Slide 76: Models Currently Implemented (April 2017)
GENERAL DATA
  CNDATA (Concentric neutral cable data)
  GROWTHSHAPE (Growth vs year)
  LINECODE (Line and cable impedances, matrices or symmetrical components)
  LINEGEOMETRY (Line geometry data)
  LINESPACING (spacing data for LINEGEOMETRY)
  LOADSHAPE (Load shape data)
  PRICESHAPE (Price shape data)
  SPECTRUM (Harmonic spectra)
  TCC_CURVE (TCC curves)
  TSDATA (Tape shield cable data)
  TSHAPE (Temperature shape data)
  WIREDATA (Wire parameters, GMR, etc.)
  XFMRCODE (Transformer type definitions)
  XYCURVE (Generic x-y curves)
METERS
  ENERGYMETER (Captures energy quantities and losses)
  MONITOR (Captures selected quantities at a point in the circuit)
  SENSOR (Simple monitor used for state estimation)
OTHER
  FAULT (1 or more faults can be placed anywhere in the circuit)
  ISOURCE (Multi-phase current source)
  VSOURCE (2-terminal multiphase voltage source, thevinen equivalent)

## Slide 77: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative solution of I=YV )
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 78: Input Data Requirements
OpenDSS is a Script-driven circuit solution engine
The OpenDSS was designed in a research or consulting environment where input data might come from a variety of sources.
The program can accept many common forms of data for describing impedances, loading, and topology of distribution systems for planning analysis.
The OpenDSS scripting language is designed to require minimal translation from other formats of distribution data.
The program can accept more detailed data for lines, transformers, etc. than the typical data for distribution system analysis when they are available.

## Slide 79: Input Data Requirements
OpenDSS Circuit elements have many properties
Nearly all have reasonable default values
Users only need to specify the property values that are
  Different than the default values
  Used in the circuit simulation
Throughout OpenDSS, property values remain at the value most recently set until they are subsequently changed
  They generally do NOT reset to original values unless you explicitly change them

## Slide 80: Advanced Types of Data in OpenDSS
Harmonic spectra for harmonic analysis,
Various curves as a function of time for sequential time simulations:
Load shapes (e.g., AMI P, Q data),
Price shapes,
Temperature shapes,
Storage dispatch curves,
Growth curves.
Efficiency curves for PV inverters,
Voltage dependency exponents for loads,
Capacitor control settings,
Regulator control settings,
TCC Curves and other data for Fuse, Relay, and Recloser objects
Machine data.

## Slide 81: How Does OpenDSS Work?

## Slide 82: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 83: Primitive Y Matrix
Simple Resistor

## Slide 84: Primitive Y Matrix, cont’d
LINE model

## Slide 85: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 86: The Network Model

## Slide 87: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 88: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 89: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 90: Load - 3-phase Y connected
Phase 1
Phase 2
Phase 3
3
2
1
4
4 Conductors/Terminal

## Slide 91: Load - 3-phase Delta connected
Phase 1
Phase 2
Phase 3
3
2
1
3 Conductors/Terminal

## Slide 92: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 93: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 94: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 95: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 96: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 97: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 98: A More Concise Form …
Fixed-point solution form for normal solution
Vn+1 = [Ysystem]-1 IPC(Vn) n = 0, 1, 2, … until converged
IPC(V) = compensation currents from Power Conversion (PC) elements in the circuit as a function of voltage

## Slide 99: Solving the Power Flow …
This solution method requires that the first guess at the voltages be close to the final solution
  Not a problem for daily or yearly simulations
    Present solution is a good initial guess at next time step
  First solution is often most difficult
The solution initialization routine in OpenDSS accomplishes this with ease in most cases
Method works well for arbitrary unbalances
  For conditions that are sensitive, a Newton method is provided that is more robust, but slower.
  Not to be confused with “Newton-Raphson Power Flow”

## Slide 100: Circuit Modeling Basics

## Slide 101: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default:
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 102: Node Numbers
The voltage at Node 0 = 0 (always)
The other Node numbers are arbitrary
By convention, Nodes 1, 2, 3 correspond to phase ABC
But they don’t have to
You can have a very large number of nodes at a Bus
They do not have to be pre-declared
Bus

## Slide 103: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 104: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 105: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 106: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
3-ph
grounded-
Wye
LOAD

## Slide 107: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load between Node 2 and ground
      Note: 1-phase Load has 2 conductors
1-Phase Load Example

## Slide 108: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 109: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node explicitly computed (just like any other Node)

## Slide 110: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 111: Capacitor Object
The Capacitor object is a basic 2-terminal branch that may be connected in different ways.
If defined with only one Bus, it is assumed to be a shunt capacitor
Same rules apply to Reactor and Fault objects

## Slide 112: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 113: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use the XfmrCode object to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 114: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 115: Scripting Basics

## Slide 116: Scripting
OpenDSS is a scriptable solution engine
Scripts
  Series of commands
  From text files
  From edit forms in OpenDSS.EXE
  From another program through COM interface
    e. g., This is how you would do looping
Scripts define circuits
Scripts control solution of circuits
Scripts specify output, etc.

## Slide 117: Command Syntax
Command parm1, parm2 parm3 parm 4 ….
Parameters may be positional or named (tagged).
If named, an "=" sign is expected.
  Name=value (this is the named form)
  Value (value alone in positional form)
For example, the following two commands are equivalent:
  New Object="Line.First Line" Bus1=b1240 Bus2=32 LineCode=336ACSR, …
  New “Line.First Line”, b1240 32 336ACSR, …
Comma or white space

## Slide 118: Delimiters
Array or string delimiter pairs: [ ] , { },( ),“ “,‘ ‘
Matrix row delimiter: |
Value delimiters: , (comma) any white space (tab or space)
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?

## Slide 119: Array and Matrix Parameters
Array
  kvs = [115, 6.6, 22]
  kvas=[20000 16000 16000]
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 120: A Simple Example

## Slide 121: A Basic Script (Class Exercise)
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements

## Slide 122: 20 MVA Substation Transformer
TR
1
New Transformer.TR1 Phases=3 Windings=2
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[20000 20000]
~ XHL=10
New Transformer.TR1 Phases=3 Windings=2 XHL=10
~ wdg=1 bus=SourceBus Conn=Delta kV=115 kVA=20000
~ wdg=2 bus= Sub_Bus Conn=wye kV=12.47 kVA=20000
Defining Using Arrays
Defining Winding by Winding
Sub_Bus
SourceBus

## Slide 123: The Line
LINE
1
1
Mile
,
336
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
Sub_Bus
LoadBus
Line objects may also be defined by Geometry or matrix properties.
(Rmatrix=… Xmatrix=… Cmatrix=…)

## Slide 124: The Load
Loadbus
LOAD
1
1000
kW
0
.
95
PF
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
For 3-phase loads, use L-L kV and total kW
For 1-phase loads, typically use L-N kV and total kW unless L-L-connected; Then use L-L kV.

## Slide 125: Add a 500-kW Generator Object to LoadBus
… (continue from existing Script)
New Generator.DG1 Bus1=LoadBus kV=12.47 kW=500 PF=1.0
// solve again and observe results
Solve ! Starts with previous solution
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
DG

## Slide 126: Scripting Large Circuits
For small circuits, it is often sufficient to put all the scripts in a single file
  Many of the IEEE test feeder examples are mostly in a single file
When you have large amounts of data, a more disciplined approach is recommended
Redirect Command
  Redirects the input to another file
  Returns to home directory
Compile Command
  Same as Redirect except repositions home directory

## Slide 127: Organizing Your Main Screen
OpenDSS.exe saves all windows on the main screen
  They appear where you left them when you shut down
  The next time you start up, you can resume your work
Values are saved to the Windows Registry

## Slide 128: OpenDSS Registry Entries
Certain persistent values are saved to the Windows Registry upon exiting the program
Default Editor Setting
After Redefining

## Slide 129: OpenDSS Main Screen
Selection to execute
Main Script Tab never goes away. Put some frequently-used commands here.
Solution Summary and Results
Results Text Box
Tabs for script files
Active Script file

## Slide 130: A Common Sense Structuring of Script Files
Run_The_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Put a “Clear” in here
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Circuit Definition
“Compile” the Master file from here
Make a separate folder for each circuit

## Slide 131: Organizing Run Scripts
Compiles the Circuit Description
Override Some Property Settings and/or Define Some Additional Circuit Element
Change an option
Solve Snapshot Power Flow
Selected Results Display
Based on 123-bus Test Feeder

## Slide 132: Organizing Your Master File
So Compile Doesn’t Fail
General Library Data
Circuit Elements for this Model
Let OpenDSS Define the Voltage Bases
(You can do this explicitly with SetkVBase command)

## Slide 133: Example: IEEE 8500-Node Test Feeder
Load and exercise the IEEE 8500-Node Test Feeder Circuit – an example of a large circuit

## Slide 134: Location of the IEEE 8500-Node Test Feeder Files

## Slide 135: Master File for 8500-Node Test Case

## Slide 136: Snippets of Circuit Script Files

## Slide 137: Circuit Plot
Plot Circuit Power Max=2000 dots=n labels=n C1=Blue 1ph=3

## Slide 138: Voltage Profile Plot
Plot profile phases=all

## Slide 139: Application Programming Interfaces (API)

## Slide 140: Why You Might Want to Write Some Code …
There is no looping in the DSS scripting language
To implement an algorithm not in OpenDSS
  For optimizing device siting …
    Generators
    Capacitors
    Reclosers
  To automate some repetitive analysis task
To develop a new device model or control
  Using the COM interface
  Writing a Dynamic-Linked Library (DLL)

## Slide 141: Ways to Write Code to Do Innovative Things with OpenDSS
COM Interface
  Microsoft standard: Windows only
  Well supported in MS Office
DirectDLL Interface
  Standard function call library
Separate program to generate DSS scripting code

## Slide 142: What Languages Can You use for Code?
Excel VBA
VB.net
C#
C/C++
Delphi, Free Pascal
MATLAB
Python
Java
LabView
R
Fortran (for DLLs, with DirectDLL)
Julia (with DirectDLL)

## Slide 143: COM Interface

## Slide 144: Finding COM Servers on Your Computer
Excel VBA

## Slide 145: Object Browser in VBA for OpenDSSEngine
The Object Browser in MS Office VBA is a good way to learn what is available through the OpenDSS COM Interface

## Slide 146: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs

## Slide 147: Demonstration of Using the COM Interface

## Slide 149: An Interesting Link Using the Direct DLL interface