## Slide 1: Advanced Modeling for Distribution Planning Workshop with OpenDSS
Instructors
Roger C. Dugan Matt Rylander
Sponsored by CenterPoint Energy At Texas A&M University April 19, 20, 21

## Slide 2: Running from MATLAB

## Slide 3: Running OpenDSS From Matlab
Starting the DSS
function [DSSStart,DSSobj,DSSText] = DSSStartup(mydir)
% Function for starting up the DSS
% make sure we are in the proper directory
cd(mydir);
%instantiate the DSS Object
DSSobj = actxserver('OpenDSSEngine.DSS');
%Start the DSS. Only needs to be executed the first time w/in a Matlab session
DSSStart = DSSobj.Start(0);
% Define the text interface
DSSText = DSSobj.Text;
%Start up the DSS
[DSSStartOK, DSSObj, DSSText] = DSSStartup(cd);

## Slide 4: Using the COM to Script Multiple Scenarios
DSSText.command = 'compile master.dss';
DSSText.command = 'New PVsystem.PV_1 phases=3 conn=delta bus1=LoadBus kV=12.47 kVA=1 Pmpp=1 pf=1';
DSSText.command = 'calcv';
DSSText.command = 'solve';
PVsize = 100:100:20001;
for ii=1:length(PVsize)
DSSText.command = ['edit PVsystem.PV_1 kVA=',num2str(PVsize(ii)*1.2),' pmpp=',num2str(PVsize(ii))];
DSSText.command = 'solve';
DSSObj.ActiveCircuit.Buses('LoadBus');
puvoltages = DSSObj.ActiveCircuit.ActiveBus.puVoltages;
puvoltage(ii) = sqrt(puvoltages(1)^2+puvoltages(2)^2);
end
Add PV system
Modify the a PV size
Compile simple circuit
Observe the feeder voltage

## Slide 5: Load Bus Voltage for Multiple Scenarios
PV @ -0.99 Power Factor
PV @ Unity Power Factor

## Slide 6: COM Server and Matlab Examples
Using Matlab

## Slide 7: Create a New Matlab .m file
DSSStartup.m must be in the same directory
First statement in the new file must activate OpenDSS COM object
The next statement checks if DSS loaded correctly and then compiles the simple feeder

## Slide 8: Communicate with the DSS Model
Select and examine an elements properties
Modify the load power factor explicitly
Modify the load power factor generically

## Slide 9: Add an Element to the Model
Text based command
  Add PV system
  Calc V to refresh voltage bases
  Modify settings
  Solve

## Slide 10: Scripting for Automated Analysis
Analyze different size PV systems to determine when ANSI voltage limits are violated
Record voltages
Record power flow

## Slide 11: Observe Results Plotted in Matlab
Power from Source
Voltage at PV Terminal

## Slide 12: Repeat with Off-nominal PV Power Factor
Voltage violation avoided by absorbing vars @ -0.99 pf
Power from Source
Voltage at PV Terminal

## Slide 13: Time Series with Variable Resource
Create a simple loadshape to simulate PV variability
%cutin and %cutout impact when the PV will be online
Setup monitors to record results
Solve
Observe results

## Slide 14: Time Series Results Plotted by DSS
Real power multiplication factors
  mult=[.1,.2,.3,.4,.5,.8,1,1,.3,.1]
  Offline in first and last interval due to cutin/cutout

## Slide 15: Adding Voltvar to the Mix
Create voltvar settings
Apply to the PV system inverter

## Slide 16: Observe Inverter Voltvar Response
Vary the system voltage
Record the inverter reactive response

## Slide 17: Observe Voltvar Response
Full reactive output above 1.03 Vpu
No reactive output from 0.99-1.01 Vpu

## Slide 18: Graphical User Interface in Matlab