## Slide 1: Advanced Modeling for Distribution Planning Workshop with OpenDSS
Instructors
Roger C. Dugan Matt Rylander
Sponsored by CenterPoint Energy At Texas A&M University April 19, 20, 21

## Slide 2: Use Cases/Examples

## Slide 3: Modeling Solar PV

## Slide 4: PVSystem in the OpenDSS
The PVSystem model combines a model of the PV array and the PV inverter into one convenient model to use for distribution system impacts studies

## Slide 5: Example Script
This example defines a PV system with a panel Pmpp of 500 kW at 1 kW/m2 irradiance and a panel temperature of 25C. The inverter is rated at 500 kVA. A PF of 1.0 is assumed for this example.
Can also be used with the InvControl control object that implements advanced (‘smart’) inverter functions such as volt-var, volt-watt, and dynamic reactive current.
InvControl usage to be covered later today

## Slide 6: Example Script
clear
New Circuit.PVSystem basekv=12.47 Isc3=1000 Isc1=900
// P-T curve is per unit of rated Pmpp vs temperature
// This one is for a Pmpp stated at 25 deg
New XYCurve.MyPvsT npts=4 xarray=[0 25 75 100] yarray=[1.2 1.0 0.8 0.6]
// efficiency curve is per unit eff vs per unit power
New XYCurve.MyEff npts=4 xarray=[.1 .2 .4 1.0] yarray=[.86 .9 .93 .97]
// per unit irradiance curve (per unit if "irradiance" property)
New Loadshape.MyIrrad npts=24 interval=1 mult=[0 0 0 0 0 0 .1 .2 .3 .5 .8 .9 1.0 1.0 .99 .9 .7 .4 .1 0 0 0 0 0]
// 24-hr temp shape curve
New Tshape.MyTemp npts=24 interval=1 temp=[25, 25, 25, 25, 25, 25, 25, 25, 35, 40, 45, 50 60 60 55 40 35 30 25 25 25 25 25 25]
// **** plot tshape object=mytemp
// take the default line
New Line.line1 Bus1=sourcebus bus2=PVbus Length=2

## Slide 7: Example Script (cont’d)
! PV definition
New PVSystem.PV phases=3 bus1=PVbus kV=12.47 kVA=500 irrad=0.8 Pmpp=500
~ temperature=25 PF=1 effcurve=Myeff P-TCurve=MyPvsT
~ Daily=MyIrrad TDaily=MyTemp
set voltagebases=[12.47]
calcv
solve ! solves at the specified irradiance and temperature
new monitor.m1 PVSystem.PV 1 mode=1 ppolar=no
new monitor.m2 PVSystem.PV 1
solve
solve mode=daily
show mon m1
show mon m2

## Slide 8: Example Script (cont’d)
Export monitors m1
Plot monitor object= m1 channels=(1 )
Export monitors m2
Plot monitor object= m2 channels=(1 ) base=[7200]
Export monitors m2
Plot monitor object= m2 channels=(9 )

## Slide 9: Modeling PV Systems – Variability/Ramping – Single-Panel

## Slide 10: Modeling PV Systems – Variability/Ramping – 1 MW PV Array (same location as Single-Panel)

## Slide 11: Modeling PV Systems – Variability/Ramping – Significance of Solar Irradiance Resolution

## Slide 12: Modeling PV Systems for Distribution System Impact Assessment – Fault Response
Fault current contribution
Conservative Rule-of-thumb: 2 x Full Output Rating of Inverter for 1 cycle (three-phase fault)
Other testing has been performed by Southern California Edison, NREL, PV inverter manufacturers, etc
Inverters generally shut down at 1.2 pu of rated current
  May be 3-4 times pre-fault current
Irregular behavior on voltage sags
  Tries to hold constant power (current increases)
  May become discontinuous

## Slide 13: Sample Open-Circuit Events – in per unit
Summarizing short circuit events: they to follow similar patterns, the event begins with a transient overcurrent, followed by a sustained current that increases (possibly an attempt to maintain output level), before the inverter trips due to voltage loss. The sustained current lasts between one and ten cycles depending on the inverter, power output level, and the triggered point-on-wave. The transient overcurrents ranged from 1.47 pu to 7.53 pu while the sustained overcurrents ranged from 0.00 pu to 1.91 pu.
Source: EPRI Protecting the Modern Distribution Grid, Program 180, 2016

## Slide 14: Sample Voltage Sag Events – Single Phase Inverters
14
90% Retained Voltage
70% Retained Voltage
60% Retained Voltage
*Dashed lines indicate the start and end of the 12 cycles sag duration
Source: EPRI Protecting the Modern Distribution Grid, Program 180, 2016

## Slide 15: ‘Smart’ Inverter Control in the OpenDSS

## Slide 16: InvControl Control Object
Works in conjunction with PVSystem object(s) to control the PVSystem(s) output according to ‘smart’ inverter functions
Three modes currently available:
  Volt-var
    Follows a voltage versus reactive power curve and changes the reactive power generation (capacitive) or reactive power absorption (inductive) according to the terminal voltage at each PVSystem
  Volt-watt
    Follows a voltage versus active power curve and changes the active power output according to the terminal voltage at each PVSystem (within the limits of the present irradiance)
  Dynamic Reactive Current (DRC)
    Has several settings that change the reactive power generation or absorption in response to fast changes in terminal voltage (e.g., during a sag or swell)

## Slide 17: Volt-var Control Mode – Example Volt-var Curve

## Slide 18: InvControl in Volt-var Mode – Script
New PVSystem.3P_ExistingSite4 phases=3 bus1=B51854_sec kV=0.4157 kVA=523 ~ irradiance=1 Pmpp=475 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite1 phases=3 bus1=X_5865228330A kV=0.4157 kVA=314 ~ irradiance=1 Pmpp=285 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite3 phases=3 bus1=X_5891328219_Cust1 kV=0.4157 ~ kVA=836 irradiance=1 Pmpp=760 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite2 phases=3 bus1=B4832_sec kV=0.4157 kVA=209 ~ irradiance=1 Pmpp=190 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New XYCurve.vv_curve npts=4 Yarray=(1.0,1.0,-1.0,-1.0) ~ XArray=(0.5,0.95,1.05,1.5)
New InvControl.InvPVCtrl mode=VOLTVAR voltage_curvex_ref=rated ~ vvc_curve1=vv_curve EventLog=yes

## Slide 19: Volt-watt Control Mode – Example Volt-watt Curve

## Slide 20: DRC Control Mode – Settings Curve

## Slide 21: Including Storage in Distribution Planning
OpenDSS STORAGE and STORAGECONTROLLER objects

## Slide 22: Introduction
Storage is the frequently-proposed solution to renewable generation issues
States and provinces are requiring large amounts of storage
  (Cal: 1.3 GW by 2020; 425 MW on distribution)
Significant amounts expected on Distribution systems controlled for benefit of Transmission

## Slide 23: Introduction, cont’d
Distribution planners are accustomed to static power flow calculations
Accurate analysis of storage required sequential-time simulation (“QSTS”)
Summary of EPRI research into modeling energy storage for planning …

## Slide 24: Applications of Storage on Distribution
Smoothing solar PV power output
Extending solar PV output into the evening
Support of the Transmission grid
Extending capacity of existing assets
Supporting alternate feeds during reconfig.
Controlling frequency of a microgrid
Increasing short circuit strength of a microgrid

## Slide 25: Planning Issues Introduced by Storage
Overvoltages while discharging
Low voltages while charging
Voltage regulation while compensating for transmission grid support
Interference with overcurrent protection scheme
Insufficient short-circuit capacity in microgrid

## Slide 26: Sequential-Time Simulation
All DER disrupt the normal load shape
A single static power flow does not give a good answer
  Have to simulate over a significant time period
Sequential-time power flow is now accepted practice in advanced distribution planning

## Slide 27: The Planning Problem with Storage is More than Capacity to meet Demand
Storage is a variable resource but it is also Limited
  Planning tools must account for energy stored
  Has a limited ramp rate
  Has to be recharged at some other time
Has losses
  Charge-discharge cycle (~15-20%)
  Idling losses (temperature dependent)

## Slide 28: 6 Simulation Modes Have Been Identified and Implemented in OpenDSS Program
  Static (charge or discharge at specific rate)
  Time (charge or discharge at specific time)
  Peak Shave
  Load Following
  Loadshape Following (define a loadshape)
  Dynamics (i.e., electromechanical transients)

## Slide 29: EPRI’s OpenDSS Employs a Generic Energy Storage Element

## Slide 30: Storage Element Operation

## Slide 31: Storage Controller Model
Fleet of Distributed Energy Storage Elements

## Slide 32: Peak Shaving Applications
Time step size: 15-60 min

## Slide 33: Compensating for Renewable Generation
Extend solar PV output into evening peak.

## Slide 34: Intermittent Generation Smoothing
PV Output
Network Response

## Slide 35: Storage Power Output for Smoothing

## Slide 36: A Dynamics Example (Black start of a Microgrid)
Model may require more than 30 parameters.

## Slide 37: Results from the Model

## Slide 38: How to Support Vendor-Supplied Models for Complex Storage System Models
Establish common software interface (DLL?)
Variants for QSTS, Dynamics, and EMT
Windows dominant platform in US for distribution
DSA vendors will have to support
Storage system vendors will want protection

## Slide 39: Simplified Distribution Planning
System Performance Considerations
  Overvoltages while discharging
  Low voltages when charging
  Voltage regulation interaction (bulk system dispatch)
  Interference with overcurrent protection
  Short circuit capacity when islanded
At least two accommodation screens:
    Max output / min load
    Max charge / max load

## Slide 40: The Versatile REACTOR Model
A Model to represent many impedance characteristics

## Slide 41: Specify R and X or Z1, Z2, Z0
Basic series R-X model
With option parallel Rp that can represent no-load losses or produce lower X/R at higher frequencies
1.. N phases
If Z2 <> Z1 then Yprim is asymmetric
Good for modeling induction machine

## Slide 42: Specify Rmatrix and Xmatrix
Can specify series (default) or parallel
Significantly different frequency response will result for parallel model
Can represent some very creative, somewhat arbitrary R-L networks.
Restricted to symmetrical at 7.6.3

## Slide 43: Dynamics Solution

## Slide 44: Dynamics Mode
Dynamics mode is used for
  Fault current calculations including Generator contributions
    Single time-step solution
  Machine transients
  Inverter transients
Typical time step: 0.2 – 1 ms
  Depends on time constants in model
A converged power flow is required to initialize the model.

## Slide 45: Basic Algorithm (From SolutionAlgs.Pas)
Increment_time;
{Predictor}
IterationFlag := 0;
IntegratePCStates;
SolveSnap;
{Corrector}
IterationFlag := 1;
IntegratePCStates;
SolveSnap;

## Slide 46: Entering Dynamics Mode
Initialize state variables in all PC Elements
  For example, in a Generator object currently:
    Compute voltage, E1, behind Xd‘ and Initialize the phase angle, , to match power flow (approximately)
Set derivatives of the state variables to zero
  For the Generator: Speed (relative to synch frequency), Angle
Set controlmode=time
  When running in time steps of a few seconds or less, controls that depend on the control queue for instructions on delayed actions will be automatically sequenced when the solution time reaches the designated time for an action to occur.

## Slide 47: 3-Phase Generator Model in Dynamics Mode
E

## Slide 48: Differential Equations for Default Generator (1-Mass)
Derivative Calculation:
Integration
Trapezoidal integration formula for , for example:

## Slide 49: User-Written DLLs
More complex behaviors can be modeled using Dynamic-Linked Libraries
Requires more sophisticated programming skills
Certain PCElements provide interfaces
  Generator, Storage
  Some Control elements, too (CapControl)
IndMach012a.DLL is an example supplied with the program
  A symmetrical component based induction machine model for the Generator class element
  (2017: now built in as a base model)

## Slide 50: Supplemental Material

## Slide 51: Harmonic Solution

## Slide 52: Solving for Harmonic Flows
The OpenDSS solution algorithm heritage
    McGraw-Edison Steady-State Analysis Program (MESSAP) 1977-78
    McGraw-Edison Harmonic Analysis Program (MEHAP) 1979-1982
    McGraw/Cooper V-Harm® program (1984)
    Electrotek Concepts SuperHarm® program (1990-92)
    Electrotek DSS (1997)
Harmonic solution has been an integral part of the program since its inception

## Slide 53: Harmonic Solution
All Load elements have ‘Spectrum=default’
  The default spectrum is a typical 3-phase ASD spectrum
  Re-define Spectrum.Default if you want something else
    Edit spectrum.default …
    Or create a new Spectrum and assign Loads to it
Harmonic solution requires a converged power flow solution to initialize all the harmonic sources
  Do “Solve mode=direct” if convergence is difficult to achieve

## Slide 54: Typical Harmonic Solution Script
Typical script for Harmonics Solution
  Solve ! Snapshot power flow
  Solve mode=harmonics
This will solve for all frequencies defined in the problem
  Make sure you have Monitors where you want to see results because results will come fast!
  Post process Monitor data in Excel, Matlab, etc. to compute THD, etc.

## Slide 55: Load Modeling for Harmonics Studies
Original Model
Present Model

## Slide 56: Transformer Modeling
There is now (as of 7.6.3.14) an option to hold X/R Constant
  More appropriate for substation transformer
  Distribution transformers have lower X/R
Modeling with Reactor
Frequency dependence is coming …

## Slide 57: What Difference Does it Make?

## Slide 58: Harmonic Solution Mode
Solve the power flow (fundamental frequency)
Harmonic current sources in LOAD models are initialized to match the fundamental frequency solution
Generators converted to Thevenin voltage behind Xd”
“Solve Mode=Harmonics”
  Program solves at each frequency that is defined
  Non-iterative (direct solution)
  Harmonic currents assumed invariant
  Y matrix is rebuilt for each frequency
  Need MONITOR objects to capture results

## Slide 59: Harmonic Solution Mode, Cont’d
Frequency Scans
  Define a scan spectrum at a small frequency increment
  Assign it to an ISOURCE or VSOURCE
  You probably want do disable LOAD and GENERATOR harmonic spectra, e.g.:
    Spectrum.DefaultLoad.NumHarm=1
    Otherwise, LOAD objects will inject a current at integer harmonic frequencies yielding a really weird solution
  Scans can be performed for (see ScanType property)
    Positive sequence
    Zero sequence
    No sequence
Example Frequency Scan
  …\Distrib\Examples\FreqScan folder

## Slide 60: Frequency Scan Example Script
// THIS SCRIPT WILL RUN A FREQUENCY SCAN ON THE IEEE 123 BUS TEST CASE
Spectrum.DefaultLoad.NumHarm=1 ! This effectively gets rid of LOAD harmonics
// Define a spectrum for the scan source
New spectrum.Scanspec numharm=1000 csvfile=ScanSpectrum.csv
// Put a Monitor to capture the results
New Monitor.Mscan Line.l84 1
// Define a positive-sequence (the default) 1-A, 3-ph current source
New Isource.scansource bus1=83 amps=1 spectrum=scanspec
solve ! solve the power flow at fundamental
solve mode=harmonics ! do the harmonic solutions
show mon mscan ! show the results
Export monitors mscan
// You can plot the Monitor, but Excel or Matlab might be better
Plot monitor object= mscan channels=(1 3 5 )

## Slide 61: What Does the Scan Spectrum Look Like?
1.083333333 100 0
1.166666667 100 0
1.25 100 0
1.333333333 100 0
1.416666667 100 0
1.5 100 0
1.583333333 100 0
1.666666667 100 0
1.75 100 0
1.833333333 100 0
1.916666667 100 0
2 100 0
2.083333333 100 0
2.166666667 100 0
2.25 100 0
2.333333333 100 0
2.416666667 100 0
2.5 100 0
2.583333333 100 0
… etc …
For 60 Hz base frequency, this gives a 5 Hz scan
Harmonic
% Magnitude
(All 100%)
Phase Angle
(All 0)
This is typically associated with a 1-A current source, so that the resulting voltages represent driving-point Z, transfer Z, etc.

## Slide 62: Putting it All Together - Harmonics
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements, each frequency
PC Elements Harmonic injection Currents
V
Node
Voltages
(each Frequency)