## Slide 1: Advanced Modeling for Distribution Planning Workshop with OpenDSS
Instructors
Roger C. Dugan Matt Rylander
Sponsored by CenterPoint Energy At Texas A&M University April 19, 20, 21

## Slide 2: “4-Wire Delta” Example

## Slide 3: The Objective of this Example
To demonstrate how to model a common transformer configuration, but one that is not covered in many textbooks
Based on the “Four Wire Center Tapped Transformer” IEEE test feeder
Point out the different voltages on the secondary.

## Slide 4: The Problem
Bank of 3 1-phase Distribution transformers
Serves both 3-phase motor load and 120/240V single phase office load

## Slide 5: Schematic

## Slide 6: Source data
12.47 kV
  Stated as “ideal”
  Zero impedance
    (Can’t model exactly in OpenDSS)

## Slide 7: Line data
Both line models are specified by 4x4 impedance matrices.
The neutral conductors are explicitly modeled
  The same phase currents can be obtained by using a Kron reduction to eliminate the neutral conductors
  Specified as 4-wire to give a challenge to distribution modeling probrams

## Slide 8: Line data – 556 MCM ACSR w/ 4/0 Neutral
(The neutral is explicitly modeled. Therefore, the matrices are 4x4, symmetrical.)
Resistance matrix (ABCN, lower triangle)
  0.2812
  0.0953 0.2812 (ohms per mile)
  0.0953 0.0953 0.2812
  0.0953 0.0953 0.0953 0.6873
Reactance matrix (ABCN, lower triangle)
  1.38304
  0.7266 1.38304 (ohms per mile)
  0.85152 0.7802 1.38304 (60 Hz)
  0.75244 0.7674 0.7864 1.54648

## Slide 9: Line data – 4/0 Quadraplex secondary
Resistance matrix (abcn, lower triangle)
  0.011
  0.0018 0.011 (ohms per 100 ft)
  0.0018 0.0018 0.011
  0.0018 0.0018 0.0018 0.013
Reactance matrix (abcn, lower triangle)
  0.0278
  0.0241 0.0278 (ohms per 100 ft)
  0.0241 0.0241 0.0278 (60Hz)
  0.0246 0.0232 0.0246 0.0293

## Slide 10: Transformer data
Center-Tapped (Lighting) transformer
  3-windings: 7200V/120V/120V, 25 kVA
The Other 2 Transformers
2 windings: 7200V/240V, 10 kVA
  Reactance: 1.4% @ 10 kVA
  Resistance: 1.6% @ 10 kVA
Windings 25 kVA X R
Primary - Secondary 1 2.04% 0.6%
Primary - Secondary 2 2.04% 1.2%
Secondary 1 - Secondary 2 1.36% 1.2%

## Slide 11: Single-Phase Loads
120V San: 3 kVA, 0.95 PF
120V Sbn: 5 kVA, 0.85 PF
240V Sab: 10 kVA, 0.90 PF

## Slide 12: 3-phase loads
Rated voltage: 240V
Per unit Impedances @ 25 kVA, 60 Hz:
  Rs=.03359397
  Xs=.07999132
  Rr=.03940972
  Xr=.07999132
  Xm=2.1
  Slip=0.035 (assumed fixed for analysis)
Connection: Assume ungrounded wye or delta (no zero sequence current).

## Slide 13: Complete Transformer Model
Yprim = A N B ZB-1 BT NT AT (3)
Yw
Y1

## Slide 14: Results – Secondary Voltages
What Reference do you choose?

## Slide 15: Individual Phase Powers (Ground Reference)
Phase | P, kW | Q, kvar
a | 2.6 | 5.8
b | 6.4 | 0.1
c | 9.8 | 6.8
Total | 18.8 | 12.7

## Slide 16: The Currents
Use the Currents to determine overload
Power flow can be confusing in such transformer configurations

## Slide 17: Together…Shaping the Future of Electricity