## Slide 1: Introduction to OpenDSS
Roger C. Dugan, LFIEEE
Sr. Technical Executive
and
Davis Montenegro, Ph.D. Engineer Scientist II
UTK Presentation, Sept 15, 2016

## Slide 2: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    As well as European-style systems
      These typically have a simpler structure

## Slide 3: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation
DG
  Interconnection studies/screening
  Value of service studies (risk based)
  Solar PV voltage rise/fluctuation
  Wind power variations impact
  Hi-penetration solar PV impacts
  Harmonic distortion
  Dynamics/islanding

## Slide 4: What can OpenDSS be used for? (cont’d)
Hybrid simulation of communications and power networks
Geomagnetically-Induced Current (GIC) flow (solar storms)
Power delivery loss evaluations (EPRI Green circuits program - > 80 feeders)
Voltage optimization
PEV/PHEV impact simulations
Community energy storage (EPRI Smart Grid Demo)
High-frequency harmonic/interharmonic interference
Various unusual transformer configurations
Transformer frequency response analysis
Distribution automation control algorithm assessment
Impact of tankless electric water heaters
Wind farm collector simulations
Wind farm interaction with transmission
Wind generation impact on capacitor switching and regulator/LTC tapchanger operations
Protection system simulation
Open-conductor fault conditions
Circulating currents on transmission skywires
Ground voltage rise during faults on lines
Stray voltage simulations
Industrial load harmonics studies/filter design
Distribution feeder harmonics analysis, triplen harmonic filter design
And many more ….

## Slide 5: The Unbalanced Distribution System
This takes more than a positive-sequence model !!

## Slide 6: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 7: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 8: Urban Low-Voltage Network Systems

## Slide 9: Computing Annual Losses
Peak load losses are not necessarily indicative of annual losses

## Slide 10: Using DSS to Determine Incremental Capacity of DG
“How much more power can be served at the same risk of unserved energy?”
Broad Summer Peaking System
“Needle” Peaking System

## Slide 11: DG Dispatch

## Slide 12: Solar PV Simulation

## Slide 13: 1-sec Solar Data – Cloud Transients
Impact on Feeder Voltage

## Slide 14: 1-sec Solar Data (2010)
Regulator Operations

## Slide 15: Power Distribution Efficiency
Light Load Week
Peak Load Week

## Slide 16: Wind Plant 1-s Simulation
Notes: The plot you see to the right is a sample case study we did where a developer wanted to install 3 750kW turbines at the end of a 10-mile distribution feeder. Along the feeder was a voltage regulator and large intermittent load. The concern we had was the impact the turbine output fluctuations would have on the flicker, regulator action, as well as the voltage profile along the feeder. Utilizing software that Electrotek had developed, specifically the Distribution System Simulator, or DSS,, minor modifications were made that allowed us to simulate the wind plant fluctuation impact over time, thus giving us the ability to address the concerns at hand.
The plot you see to the right is simulation output from the DSS, over a time horizon of ~ 4 minutes. The three turbines were modeled explicitly, along with the 5-step switched capacitor banks connected to each turbine as well as the voltage regulator upline from the wind plant. This software allows us to make recommendations to the utility and/or wind plant developer regarding modifications necessary, if any, to allow for the wind plant to have minimal impact on the distribution feeder and surrounding customers, or perhaps even improve feeder performance.
We also utilize this software for estimating flicker according the IEC standard 1400-21. The software, along with data specific to the turbine being considered allows one to estimate the flicker impact BEFORE the turbine is installed.

## Slide 17
Broadband Driving Point Admittance
0
0.005
0.01
0.015
0.02
0.025
0.03
0.035
0
100000
200000
300000
400000
500000
Frequency, Hz
Siemens
|Y|

## Slide 18: Power Flow Visualization

## Slide 19: Special Displays
Fault Current Magnitudes

## Slide 20: Example of an Expected DG Problem
Regulator taps up to compensate for voltage drop
Voltage overshoots as power output ramps up

## Slide 21: Root of Problem
Voltage Profile w/ DG
0.0
2.0
4.0
6.0
Distance from Substation (km)
0.90
0.95
1.00
1.05
1.10
p.u. Voltage
High Voltages
Distribution Systems designed for voltage DROP, not voltage RISE.

## Slide 22: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose: DG interconnection analysis

## Slide 23: What is the OpenDSS? (cont’d)
What it Isn’t
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a Power Flow program
  Not a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 24: Time- and Location-Dependent Benefits
The OpenDSS was designed to capture both
  Time-specific benefits and
  Location-specific benefits
Needed for
  DG analysis
  Renewable generation
  Energy efficiency analysis
  PHEV and EV impacts
  Other proposed capacity enhancements that don’t follow typical loadshapes

## Slide 25: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak loading conditions
  Capture mostly location-specific benefits
  Ignores time; Assumes resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do time sequence analysis to get the right answer
  Over distribution planning area

## Slide 26: What are the Key Features?
See Documentation for more details
  http://svn.code.sf.net/p/electricdss/code/trunk/Distrib/Doc/
Designed to allow expansion indefinitely
  Impossible to anticipate everything users will want to do
  COM interface allows easier customization

## Slide 27: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 28: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 29: Overall Model Concept

## Slide 30: User Interfaces Currently Implemented
A stand-alone executable program that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
Direct DLL (standard Windows DLL)
  Mimics COM interfaces

## Slide 31: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYMDIST, SYNERGEE, and WindMil programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Being used to develop the DG Protection test feeder and the large urban network test feeder.
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data.
Recently, the new PVSystem model was compared to actual measurements with excellent results.

## Slide 32: Needs Envisioned by EPRI for the Smart Grid
Sequential time simulation
Meshed network solution capability
Better modeling of Smart Grid controllers
Advanced load and generation modeling
High phase order modeling ( >3 phases)
  Stray voltage (NEV), crowded ROWs, etc.
Integrated harmonics
  NEV requires 1st and 3rd
User-defined (scriptable) behavior
Dynamics for DG evaluations

## Slide 33: EPRI’s Vision
Distribution planning and distribution management systems (DMS) will converge
  Into a unified set of analysis tools.
Real-time analysis and planning analysis will merge into common tools.
Distribution system analysis tools will continue to play an important role,
  Although they might appear in a much different form than today.

## Slide 34: Plan for Future Work/Enhancements
There is a continuing effort to promote interfacing to the Common Information Model (CIM).
  The CIM is the common data interchange mechanism
We plan to exploit high performance desktop computing to make it feasible to study distribution systems of at least 100,000 nodes and perhaps as many as 1,000,000 nodes.
  This will involve revamping algorithms within the program to enable the application of parallel processing (multiple CPUs) to planning problems.
    e.g., Diakoptics
Improved distribution state estimation functions
Improved Distribution Management Systems (DMS) functions

## Slide 35: What’s Next?
It’s time to address other Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”

## Slide 36: Getting Started: Installation and Basic Usage

## Slide 38: Main Download Page

## Slide 39: OpenDSS downloads
Downloads Continue to Accelerate
Estimate: ~ 2000 active users World-Wide at any time
More and more profs assigning projects each year

## Slide 40: OpenDSS downloads - Countries

## Slide 41: How Does OpenDSS Work?

## Slide 42: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 43: Primitive Y Matrix
Simple Resistor

## Slide 44: Primitive Y Matrix, cont’d
LINE model

## Slide 45: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 46: The Network Model

## Slide 47: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 48: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 49: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 50: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 51: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 52: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 53: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 54: Together…Shaping the Future of Electricity