## Slide 1: Intro to OpenDSS Workshop
Roger Dugan Sr. Technical Exec. EPRI
Milsoft User’s Conference Orlando, FL June 9, 2016

## Slide 2: OpenDSS
DSS was developed in 1997 to enable analysis of disruptive technologies such as DER
DSS acquired by EPRI in 2004
Made open source and renamed OpenDSS in 2008
  To speed industry advancements in grid modernization
  Over 35,000 downloads since 2008
  > 170 countries
  US, China, Canada, and UK lead in downloads
47,000
Brazil and India

## Slide 3: Country List …

## Slide 4: What Can You Do with OpenDSS?

## Slide 5: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation

## Slide 6: What has OpenDSS be used for?
Hybrid simulation of communications and power networks
Geomagnetically-Induced Current (GIC) flow (solar storms)
Power delivery loss evaluations (EPRI Green circuits program - > 80 feeders)
Voltage optimization
PEV/PHEV impact simulations
Community energy storage (EPRI Smart Grid Demo)
High-frequency harmonic/interharmonic interference
Various unusual transformer configurations
Transformer frequency response analysis
Distribution automation control algorithm assessment
Impact of tankless electric water heaters
Wind farm collector simulations
Wind farm interaction with transmission
Wind generation impact on capacitor switching and regulator/LTC tapchanger operations
Protection system simulation
Open-conductor fault conditions
Circulating currents on transmission skywires
Ground voltage rise during faults on lines
Stray voltage simulations
Industrial load harmonics studies/filter design
Distribution feeder harmonics analysis, triplen harmonic filter design
And many more ….

## Slide 7: What’s Next?
It’s time to address other Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”

## Slide 8: EPRI’s Vision
Distribution planning and distribution management systems (DMS) will converge
  Into a unified set of analysis tools.
Real-time analysis and planning analysis will merge into common tools.
Distribution system analysis tools will continue to play an important role,
  Although they might appear in a much different form than today.

## Slide 9: Computing Annual Losses
Peak load losses are not necessarily indicative of annual losses

## Slide 10: Using DSS to Determine Incremental Capacity of DG
“How much more power can be served at the same risk of unserved energy?”
Broad Summer Peaking System
“Needle” Peaking System

## Slide 11: DG Dispatch

## Slide 12: Solar PV Simulation – 1 h step size

## Slide 13: 1-s Solar Data – Cloud Transients
Impact on Feeder Voltage ??

## Slide 14: 1-sec Solar Data (2010)
Regulator Operations

## Slide 15: Root of Problem
Voltage Profile w/ DG
0.0
2.0
4.0
6.0
Distance from Substation (km)
0.90
0.95
1.00
1.05
1.10
p.u. Voltage
High Voltages
Distribution Systems designed for voltage DROP, not voltage RISE.

## Slide 16: Power Distribution Efficiency
Light Load Week
Peak Load Week

## Slide 17: Wind Plant 1-s Simulation
Notes: The plot you see to the right is a sample case study we did where a developer wanted to install 3 750kW turbines at the end of a 10-mile distribution feeder. Along the feeder was a voltage regulator and large intermittent load. The concern we had was the impact the turbine output fluctuations would have on the flicker, regulator action, as well as the voltage profile along the feeder. Utilizing software that Electrotek had developed, specifically the Distribution System Simulator, or DSS,, minor modifications were made that allowed us to simulate the wind plant fluctuation impact over time, thus giving us the ability to address the concerns at hand.
The plot you see to the right is simulation output from the DSS, over a time horizon of ~ 4 minutes. The three turbines were modeled explicitly, along with the 5-step switched capacitor banks connected to each turbine as well as the voltage regulator upline from the wind plant. This software allows us to make recommendations to the utility and/or wind plant developer regarding modifications necessary, if any, to allow for the wind plant to have minimal impact on the distribution feeder and surrounding customers, or perhaps even improve feeder performance.
We also utilize this software for estimating flicker according the IEC standard 1400-21. The software, along with data specific to the turbine being considered allows one to estimate the flicker impact BEFORE the turbine is installed.

## Slide 18: Storage Modeling Simple Peak Shave Example

## Slide 19: Dynamics Storage Simulation
(Requires separately-licensed DLL)

## Slide 20: Getting Started

## Slide 21: Installing
EPRI Link Page
    http://smartgrid.epri.com/SimulationTool.aspx

## Slide 22: SourceForge.Net Links for OpenDSS
EPRI Links Page
  http://smartgrid.epri.com/SimulationTool.aspx
OpenDSS Download Files:
  http://sourceforge.net/projects/electricdss/files/
Top level of Main Repository

## Slide 23: Install Both 32-bit and 64-bit Versions of OpenDSS
DG Screener and Excel typically use 32-bit OpenDSS, but both versions must be installed to get 32-bit server fully installed. Windows will figure out which one needs to be executed. Magic!!

## Slide 24: OpenDSS Files Installed
Main Program Files

## Slide 25: Key Files in Doc Folder
Getting Started With OpenDSS.pdf
OpenDSSPrimer.pdf
OpenDSSManual.pdf
OpenDSS Cheatsheet.pdf

## Slide 26: Discussion Forum & News for OpenDSS

## Slide 27: Introduction to Distribution Systems and Modeling

## Slide 28: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, Synergi, WindMil, and other programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Being used to develop the DG Protection test feeder
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data.

## Slide 29: OpenDSS is Basically a Nodal Admittance Solver
OpenDSS is a script-driven, frequency-domain electrical circuit simulation tool
  It uses a basic nodal admittance circuit model that could be used for a wide variety of ac circuit analysis applications
OpenDSS has specific models for:
  Supporting utility distribution system analysis
  Initially designed for the unbalanced, multi-phase North American power distribution systems
  Can also model European-style systems
      These typically have a simpler structure

## Slide 30: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 31: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 32: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 33: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 34: What is the OpenDSS?
Heritage of OpenDSS
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve the power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose in 1997: DG interconnection analysis

## Slide 35: What is the OpenDSS? (cont’d)
What it is NOT
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics” mode
      All solutions are in phasors (complex math)
  Not a “Power Flow” program
  Not a radial circuit solver
    Does meshed networks with equal ease
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 36: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonics
Custom user-defined solutions

## Slide 37: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
  Storage controllers
  Inverter control
  Switch control
  Relays, Reclosers, and Fuses are controls

## Slide 38: Overall Model Concept (1997)

## Slide 39: Control Modes
Static
  Power flows with large time steps
Time
  Control queue employed to delay actions
  Control acts when time is reached
Event

## Slide 40: User Interfaces Currently Implemented
A stand-alone executable program that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  32-bit and 64-bit (New in 2012)
A Direct DLL interface for user-written programs on HPCs and servers
EPRI Program 174 funders have access to DGScreener, an interface to OpenDSS

## Slide 41: Why Scripting and COM?
More flexible than static dialog forms
No two Smart Grid simulations alike
Not possible to predict what users will want to do
  COM = Component Object Model
  Supported by nearly all programming languages, Microsoft Office, MATLAB, Python, etc that run on Windows
  Allows user to write their own algorithms
    For things like DA controllers and DMS simulators
    Co-simulation of power and communications
  COM is not familiar to most power engineers but is powerful means of scripting

## Slide 42: What is COM?
COM = Component Object Model
A binary-interface standard for software components introduced by Microsoft in 1993
Related technologies
  OLE, OLE Automation, ActiveX, COM+, DCOM
A language-neutral way of implementing objects that can be used in environments different from the one in which they were created
Microsoft Office tools like Excel and Work can be Automated via COM
  And VBA supports automating other apps via COM

## Slide 43: How Does OpenDSS Work?

## Slide 44: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 45: Primitive Y Matrix
Simple Resistor

## Slide 46: Primitive Y Matrix, cont’d
LINE model

## Slide 47: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 48: The Network Model

## Slide 49: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 50: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 51: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 52: Load - 3-phase Y connected
Phase 1
Phase 2
Phase 3
3
2
1
4
4 Conductors/Terminal

## Slide 53: Load - 3-phase Delta connected
Phase 1
Phase 2
Phase 3
3
2
1
3 Conductors/Terminal

## Slide 54: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 55: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 56: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 57: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 58: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 59: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 60: Circuit Modeling Basics in OpenDSS

## Slide 61: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 62: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 63: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 64: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 65: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
LOAD

## Slide 66: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load to Node 2 and ground
1-Phase Load Example

## Slide 67: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 68: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node is explicitly computed (just like any other Node)

## Slide 69: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 70: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 71: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use XfmrCode to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 72: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 73: OpenDSS Scripting Basics
Example Circuit

## Slide 74: A Basic Script
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
Var @MV1=12.47
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 @MV1]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
set voltagebases=[115 @MV1]
Calcvoltagebases
Solve

## Slide 75: Scripting for Larger Circuits
How to organize scripts for larger problems
Examination of how the IEEE 8500-Node Test Feeder model is organized

## Slide 76: Scripting Large Circuits
For small circuits, often put all the scripts in one file
  Some IEEE test feeder examples are mostly in one file
When you have large amounts of data, a more disciplined approach is recommended using multiple files:
Redirect Command
  Redirects the input to another file
  Returns to home directory
Compile Command
  Same as Redirect except repositions home directory

## Slide 77: Organizing Your Main Screen
OpenDSS.exe saves all windows on the main screen
  They appear where you left them when you shut down
  The next time you start up, you can resume your work
Values are saved in the Windows Registry
Come up with a way you are comfortable with

## Slide 78: A Common Sense Structuring of Script Files
Run_The_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Put a “Clear” in here
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Circuit Definition
“Compile” the Master file from here
Make a separate folder for each circuit

## Slide 79: Organizing Your Master File
So Compile Doesn’t Fail
General Library Data
Circuit Elements for this Model
Let OpenDSS Define the Voltage Bases
(You can do this explicitly with SetkVBase command)

## Slide 80: Example: IEEE 8500-Node Test Feeder

## Slide 81: Main Part of “Run” File
Compile (C:\DSSdata\IEEETest\8500Node\Master-unbal.dss)
! Put an Energymeter at the head of the feeder New Energymeter.m1 Line.ln5815900-1 1
! Sometimes the solution takes more than the default 15 iterations Set Maxiterations=20
Solve
Compile base circuit description
Add an energymeter not in base description
Change an option
Solve

## Slide 82: The Master File
Clear
New Circuit.IEEE8500u
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.dss
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
Redirect LoadXfmrs.dss ! Load Transformers
Redirect Triplex_Lines.dss
Redirect UnbalancedLoads.dss
Redirect Capacitors.dss
Redirect CapControls.dss
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordintes now that bus list is established
Buscoords Buscoords.dss

## Slide 83: DGScreener Connection to OpenDSS
An Example of COM Interface Driver

## Slide 84: DG Screener Structure
OpenDSS
DG Screener
DSS Scripts
(Text)
OpenDSS COM Interface
Circuit Templates and Case Files
General OpenDSS Files

## Slide 85: OpenDSS COM Interface

## Slide 86: Two Implementations of OpenDSS
Stand-alone EXE
  32-bit
  64-bit
  Use this to develop text scripts to study problems
In-Process COM Server
  32-bit
  64-bit
  Use this to link OpenDSS to other programs
    Automate the program
    Execute complex algorithms

## Slide 87: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs
Text

## Slide 88: OpenDSSEngine.DSS is Registered
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 89: Linking Your Program to the COM Server
Examples of accessing the COM server in various languages
In MATLAB:
  DSSobj = actxserver(‘OpenDSSEngine.DSS’);
In VBA:
  Public DSSobj As OpenDSSEngine.DSS Set DSSobj = New OpenDSSEngine.DSS
In Dephi
  {Import Type Library}
  Type DSSObj : IDSS;  This is how DG Screener does it!
  …
  DSSObj := coDSS.Create;

## Slide 90: Linking Your Program to the COM Server, 2
In PYTHON:
  Import win32com.client
  Class DSS:
  self.engine = win32com.client.Dispatch("OpenDSSEngine.DSS")
In C#:
  (Project >Add Reference … select OpenDSSEngine)
  Using OpenDSSEngine;
  Public DSS DSSObj;
  DSSObj = new DSS();

## Slide 91: OpenDSS COM Interfaces
There are many interfaces supplied by the COM server
There is one registered In-Process COM interface:
  OpenDSSEngine.DSS
    The DSS interface is the one your program instantiates
    The DSS interface then creates all the others.
    This is for simplicity for users who are not necessarily familiar with COM programming

## Slide 92: “Active objects” concept
.The interfaces generally act on the ACTIVE object
  Active circuit,
  Active circuit element,
  Active bus, etc.
The interfaces generally point to the active object
  To work with another object, change the active object
    There are methods for selecting objects
    You may also use script commands

## Slide 93: Viewing the COM Interface
The easiest way for most users to view the OpenDSS COM interface is to use Microsoft Excel
Procedure
  Start Excel
  Alt-F11 to open VBA Editor
  Connect to OpenDSS Engine via Tools>References

## Slide 94: Loadshapes and Smart Grid Simulation: The Key to Dynamic Modeling

## Slide 95: Modeling Solar PV

## Slide 96: PVSystem in the OpenDSS
The PVSystem model combines a model of the PV array and the PV inverter into one convenient model to use for distribution system impacts studies

## Slide 97: Example Script
This example defines a PV system with a panel Pmpp of 500 kW at 1 kW/m2 irradiance and a panel temperature of 25C. The inverter is rated at 500 kVA. A PF of 1.0 is assumed for this example.
Can also be used with the InvControl control object that implements advanced (‘smart’) inverter functions such as volt-var, volt-watt, and dynamic reactive current.
InvControl usage to be covered later today

## Slide 98: Example Script
clear
New Circuit.PVSystem basekv=12.47 Isc3=1000 Isc1=900
// P-T curve is per unit of rated Pmpp vs temperature
// This one is for a Pmpp stated at 25 deg
New XYCurve.MyPvsT npts=4 xarray=[0 25 75 100] yarray=[1.2 1.0 0.8 0.6]
// efficiency curve is per unit eff vs per unit power
New XYCurve.MyEff npts=4 xarray=[.1 .2 .4 1.0] yarray=[.86 .9 .93 .97]
// per unit irradiance curve (per unit if "irradiance" property)
New Loadshape.MyIrrad npts=24 interval=1 mult=[0 0 0 0 0 0 .1 .2 .3 .5 .8 .9 1.0 1.0 .99 .9 .7 .4 .1 0 0 0 0 0]
// 24-hr temp shape curve
New Tshape.MyTemp npts=24 interval=1 temp=[25, 25, 25, 25, 25, 25, 25, 25, 35, 40, 45, 50 60 60 55 40 35 30 25 25 25 25 25 25]
// **** plot tshape object=mytemp
// take the default line
New Line.line1 Bus1=sourcebus bus2=PVbus Length=2

## Slide 99: Example Script (cont’d)
! PV definition
New PVSystem.PV phases=3 bus1=PVbus kV=12.47 kVA=500 irrad=0.8 Pmpp=500
~ temperature=25 PF=1 effcurve=Myeff P-TCurve=MyPvsT
~ Daily=MyIrrad TDaily=MyTemp
set voltagebases=[12.47]
calcv
solve ! solves at the specified irradiance and temperature
new monitor.m1 PVSystem.PV 1 mode=1 ppolar=no
new monitor.m2 PVSystem.PV 1
solve
solve mode=daily
show mon m1
show mon m2

## Slide 100: Example Script (cont’d)
Export monitors m1
Plot monitor object= m1 channels=(1 )
Export monitors m2
Plot monitor object= m2 channels=(1 ) base=[7200]
Export monitors m2
Plot monitor object= m2 channels=(9 )

## Slide 101: Modeling PV Systems – Variability/Ramping – Single-Panel

## Slide 102: Modeling PV Systems – Variability/Ramping – 1 MW PV Array (same location as Single-Panel)

## Slide 103: Modeling PV Systems – Variability/Ramping – Significance of Solar Irradiance Resolution

## Slide 104: Modeling PV Systems for Distribution System Impact Assessment – Fault Response
Fault current contribution
‘Rule-of-thumb’: 2 x Full Output Rating of Inverter for 1 cycle (three-phase fault)
Other testing has been performed by Southern California Edison, NREL, PV inverter manufacturers, etc
NREL
  1 kW inverter: 4 x pre-fault output current for 1.6 ms
PV Inverter Manufacturer (un-named)
  500 kva grid-tied: 2 – 3 times pre-fault output current for up to 4.25 ms

## Slide 105: Modeling PV Systems for Distribution System Impact Assessment – Harmonic Response
Single units – Model as current sources
  Typically below IEEE 519-1992 current injection limits for generation equipment, especially at low harmonic orders
  Multiple units – Model as current sources with cancellation at higher order harmonics

## Slide 106: Modeling PV Systems for Distribution System Impact Assessment – Anti-Islanding
Difficult to model without explicit knowledge of the anti-islanding scheme implementation details for the PV System
Implementation details for the PV Systems are usually ‘trade secrets’ and therefore not publicly available for use
See, for more information on approaches: “Evaluation of Islanding Detection Methods for Photovoltaic Utility Interactive Power Systems”, International Energy Agency, March 2002.
Precise re-creation of events in EMTP-like programs, from ‘in-the-field’ system event recordings will likely be difficult with generic models of anti-islanding approaches

## Slide 107: ‘Smart’ Inverter Control in the OpenDSS
InvControl

## Slide 108: InvControl Control Object
Works in conjunction with PVSystem object(s) to control the PVSystem(s) output according to ‘smart’ inverter functions
Three modes currently available:
  Volt-var
    Follows a voltage versus reactive power curve and changes the reactive power generation (capacitive) or reactive power absorption (inductive) according to the terminal voltage at each PVSystem
  Volt-watt
    Follows a voltage versus active power curve and changes the active power output according to the terminal voltage at each PVSystem (within the limits of the present irradiance)
  Dynamic Reactive Current (DRC)
    Has several settings that change the reactive power generation or absorption in response to fast changes in terminal voltage (e.g., during a sag or swell)

## Slide 109: Volt-var Control Mode – Example Volt-var Curve

## Slide 110: InvControl in Volt-var Mode – Script
New PVSystem.3P_ExistingSite4 phases=3 bus1=B51854_sec kV=0.4157 kVA=523 ~ irradiance=1 Pmpp=475 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite1 phases=3 bus1=X_5865228330A kV=0.4157 kVA=314 ~ irradiance=1 Pmpp=285 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite3 phases=3 bus1=X_5891328219_Cust1 kV=0.4157 ~ kVA=836 irradiance=1 Pmpp=760 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite2 phases=3 bus1=B4832_sec kV=0.4157 kVA=209 ~ irradiance=1 Pmpp=190 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New XYCurve.vv_curve npts=4 Yarray=(1.0,1.0,-1.0,-1.0) ~ XArray=(0.5,0.95,1.05,1.5)
New InvControl.InvPVCtrl mode=VOLTVAR voltage_curvex_ref=rated ~ vvc_curve1=vv_curve EventLog=yes

## Slide 111: Volt-watt Control Mode – Example Volt-watt Curve

## Slide 112: DRC Control Mode – Settings Curve

## Slide 113: Scripting Storage Models
See “OpenDSS STORAGE Element.PDF” in Distrib\DOC folder

## Slide 114: Storage Element Model in EPRI’s OpenDSS
% Eff. Charge/Discharge
Idle | Discharge | Charge
Idling Losses
kW, kvar
kWh STORED
Other Key Properties
% Reserve kWhRated kWhStored %Stored kWRated
etc.

## Slide 115: StorageController Element in OpenDSS
Discharge Mode Charge Mode kW Target Discharge Time Total Fleet kW Capacity Total Fleet kWh
et. al.
Storage “Fleet”
Substation
V, I
Comm Link
Time + Discharge rate Peak Shaving Load Following Loadshape

## Slide 116: Simple Peak Shave Example with 3-Hour Storage
From EPRI
Smart Grid Demo - AEP
Community Energy Storage

## Slide 117: Detail on Peak Shaving Application

## Slide 119
“Ran Out of Gas”

## Slide 121
12:00 is too early
Load declines after 12:00

## Slide 122: Using Storage to Extend Solar PV
Source: EPRI, 2012, Analysis of Distribution System Effects of Energy Storage Through Simulation and Modeling, Palo Alto, CA, US. 1024285

## Slide 123: Using Storage for Smoothing PV

## Slide 124: Storage with Controller
Clear
New Circuit.TestStorage
~ BasekV=12.47
New Line.Line1 Bus1=Sourcebus LoadBus ! default line
New Loadshape.DailyShape npts=96 minterval=15 mult=[file=storagetestshape.csv]
New Storage.Battery phases=3 Bus1=loadbus kV=12.47 kW=250 kWrated=250 kWhrated=1000
~ dispmode=follow daily=dailyshape
set voltagebase=[12.47]
calcv
new monitor.PQ storage.battery 1 ppolar=no mode=1
new monitor.Vars storage.battery 1 mode=3
solve
solve mode=daily step=15m number=(2 96 *)
show mon PQ
show mon vars

## Slide 125: The Loadshape

## Slide 126: Result …

## Slide 127: Storage with DynaDLL
clear
New Circuit.SimpleStore ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.02 ISC3=30000 ISC1=25000 !Define source V and Z
New Transformer.TR1 XHL=10
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[200000 200000]
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=0.011 Units=Mi
New Transformer.MVLV XHL = 5
~ Buses=[LoadBus LVBus]
~ Conns=[Delta Wye]
~ kVs= [12.47 .400]
~ kVAs=[300 300]
New Storage.Store1 phases=3 Bus1=LVBus kV=0.400 conn=Delta kVA=60
~ kWrated=60 kWHrated= 0.20833 %reserve=50 // 750 kW-s (kJ)
~ state=discharge
~ kW=50 PF=1
~ DynaDLL="C:\Users\prdu001\OpenDSS\Source\DESS1\Dess1.DLL"
! ~ DynaData=(help)
~ DynaData=(file=DESSModel_Test.TxT)
// New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95 model=4 cvrwatts=1.2
Solve

## Slide 128: Storage with Controller
new Storage.battery phases=3 bus1=loadbus kv=12.47
~ kwrated=250 kwhrated=1000
new StorageController.battery element=line.Line1
~ %Reserve=20.0
~ ModeCharge=Loadshape
~ ModeDischarge=Loadshape
~ Yearly=ls_bat_cntrl
~ EventLog=Yes

## Slide 129: Model for Direct-Connect Y-connected DG to avoid convergence issue
Insert a Yn-D Transformer in Series with delta-connected DG to achieve Y direct to avoid numerical problems in OpenDSS. Set Transformer XHL = DG’s %X0

## Slide 130: Monte Carlo Fault Example

## Slide 131: Concept: One-Line Diagram